May 18, 2005

Mr. Grant H. Weaver
RA&MCO Insurance Services
2300 Clayton Road, Ste 1100

Concord, CA  94520
RE:
Policy No. EDN 5656039 01
Gentlemen,

On or about November 25, 2003, Dammon Engineering completed the design of a buildout for a restaurant called the “China King,” located at 39510 Hwy 190 East, Slidell, Louisiana.  Our contract was with the General Contractor (K.B. Kaufmann Construction) for the shopping center, and the buildout of the restaurant, as we designed both.

Our employees met with the General Contractor and the restaurant owner, who was leasing space for his restaurant, to discuss his requirements, and one item discussed was that he would order and have installed, the kitchen hood, with make-up air, etc., so that the air conditioning system would not have to compensate for air leaving the kitchen by way of the hood.

This being accomplished, we provided a design for this small restaurant that was in line with the needs of that type restaurant.

Construction was completed and after opening, the shopping center owner informed the General Contractor that the hood was sucking conditioned air out of the kitchen and the dining area.  We, along with the General Contractor, investigated and found the hood to pull excessive amounts of air from the facility.

I hired a mechanical engineer, who does other work for me, to investigate the hood and give an opinion.  His fee was $2,397.50.  The General Contractor hired an air conditioning company to install additional air conditioning in the restaurant to fix the problems around July – August, 2004.  The General Contractor asked that we pay $9,000.00 to help him fix the problem, and we did.  Actually, we provided credit on other work, as we do many projects for and with him.

The General Contractor had hired an independent Mechanical Engineer to give his opinion.  This engineer later switched sides and designed a completely new A/C system for the restaurant, for the owner of the building.  I have not seen his design and do not know if they installed it.

It has now come to light that the building owner is suing the General Contractor about this matter and possibly other matters she supposedly had problems with.  The General Contractors insurance company now is asking for our insurer to get involved.  I am not sure that a suit has been filed.
Sincerely,

Emmett G. (Pete) Dammon, P.E.
Plaintiff:
GLBJ, LLC


Attorney:



Jeansonne & Remondet



c/o Mr. Scott Higgens



P.O. Box 91530



Lafayette, LA  70509



(317) 237-4370

Defendant:
K.B. Kaufmann & Co.



1019 Old Spanish Trail



Slidell, LA  70458



Attorney:



Hulse & Wanek


c/o Mr. Steve Mogabgab



512 E. Boston Street



Covington, LA  70433



(985) 893-2932

