Eaton Electrical / Cutler Hammer
3500 N.Causeway Blvd. Suite 540
Metairie, LA 70002
.
Job Name:  Chalmette ES
Comments & Clarifications



 1
Enclosed Breakers
Factory Assembled Enclosed Circuit Breaker
Catalog Number SNHFD3045LS06
480Volts, 45Amps, 3 Pole, 65 KAIC
Designations: 
45 A 3P ECB


1
Enclosed Breakers
Factory Assembled Enclosed Circuit Breaker
Catalog Number SNHFD3070LS06
480Volts, 70Amps, 3 Pole, 65 KAIC
Designations: 
70A 3P ECB


6
Side Mounted TVSS
Catalog Number:  CPS100208YSK
Clipper Visor Series; 100 kA; 120/208V; Wye, Grounded Winding; NEMA 1, 3R Rainproof Enclosure 
Designations: 
TVSS-LP1, TVSS-LP2, TVSS-LP3, TVSS-LP4, TVSS-LP5, TVSS-2LP1


3
Dry Type Transformer
Standard Transformer Catalog Number:  V48M28F30CUEEES
Transformer Type: General Purpose Vented
3 PHASE, 30 KVA, 480 Primary Volts, 208Y/120 Secondary Volts, 
115C Temperature Rise, Copper Winding Material, NEMA 2 (N3R w/opt'l weathershield) Enclosure Type, 60 HZ,
Frame 912B, Wiring Diagram 283B
Designations: 
TSB, T4, T5A


4
Dry Type Transformer
Standard Transformer Catalog Number:  V48M28F45CUEEES
Transformer Type: General Purpose Vented
3 PHASE, 45 KVA, 480 Primary Volts, 208Y/120 Secondary Volts, 
115C Temperature Rise, Copper Winding Material, NEMA 2 (N3R w/opt'l weathershield) Enclosure Type, 60 HZ,
Frame 912B, Wiring Diagram 283B
Designations: 
TK, T3, T4, T5


2
Dry Type Transformer
Standard Transformer Catalog Number:  V48M28F75CUEEES
Transformer Type: General Purpose Vented
3 PHASE, 75 KVA, 480 Primary Volts, 208Y/120 Secondary Volts, 
115C Temperature Rise, Copper Winding Material, NEMA 2 (N3R w/opt'l weathershield) Enclosure Type, 60 HZ,
Frame 914D, Wiring Diagram 283B
Designations: 
2T1, T2


1
Dry Type Transformer
Custom Transformer, Style Number Y48G28T06CU
Similar To Standard Transformer Y48G28T06N
Transformer Type: General Purpose Encapsulated
3 PHASE, 6 KVA, 480 Primary Volts, 208Y/120 Secondary Volts, 
115C Temperature Rise, Copper Winding Material, NEMA 3R Encapsulated Enclosure Type, 60 HZ,
Frame 200, Wiring Diagram 70A
Designations: 
TEM4


2
Dry Type Transformer
Custom Transformer, Style Number Y48G28T03CU
Similar To Standard Transformer Y48G28T03N
Transformer Type: General Purpose Encapsulated
3 PHASE, 3 KVA, 480 Primary Volts, 208Y/120 Secondary Volts, 
115C Temperature Rise, Copper Winding Material, NEMA 3R Encapsulated Enclosure Type, 60 HZ,
Frame 201, Wiring Diagram 70A
Designations: 
TEM5, TEM


1
Enclosed Control
NEMA - Freedom, NEMA 1 - General Purpose, 10 HP,  460V,  Size 1
120V/60 110V/50 Coil,   30A 600v Class RDisconnect
Drawing Number:  84-28780
Designations: 



1
Enclosed Control
Lighting, NEMA 1 - General Purpose, 9 Pole, 460V,  30A
120V/60 110V/50 Coil
Drawing Number:  84-28696
Designations: 
LC-1


1
Eaton Electrical Startup Services
Eaton Electrical Standard scope of work, 1 engineers, 3 on-site testing days, Baton Rouge, LA 

Designations: 
START UP


1
Freedom MCC
60 Hz, Class 1B wiring, 480V 3-Phase Service, 42,000 Bracing, Top Incoming,
NEMA 1 Gasketed 16" Front Mt Only enclosure, 600A Copper Main Horizontal Bus,
No Neutral, Main Lugs
Designations: 
MCC-M


1
Pushbutton Station
Catalog Number:  

Designations: 
E-STOP BUTTON


1
Pow-R-Line3a
42 Circuits, 400A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 50k AIC,400A, Main Lugs Only[Top Fed], 400A, Through-Feed Lugs, Surface Mounted
Designations: 
HP1-SEC-1


1
Pow-R-Line3a
42 Circuits, 400A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 50k AIC,400A, Main Lugs Only[Top Fed], Surface Mounted
Designations: 
HP1-SEC-2


1
Pow-R-Line3a
27 Circuits, 100A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 25k AIC,70A, FD 3P Main Breaker[Top Fed], Surface Mounted
Designations: 
EMH


2
Pow-R-Line2a
30 Circuits, 100A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 14k AIC,100A, Main Lugs Only[Top Fed], Surface Mounted
Designations: 
EMH4, EMH5


1
Pow-R-Line1a
18 Circuits, 100A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,20A, 3P BAB-H Main Breaker[Top Fed], Surface Mounted
Designations: 
EML


1
Pow-R-Line1a
30 Circuits, 100A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,25A, 3P BAB-H Main Breaker[Top Fed], Surface Mounted
Designations: 
EML4


1
Pow-R-Line1a
30 Circuits, 100A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,20A, 3P BAB-H Main Breaker[Top Fed], Surface Mounted
Designations: 
EML5


1
Pow-R-Line1a
42 Circuits, 225A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,110A, 3P EDB Main Breaker[Top Fed], Surface Mounted
Designations: 
LP1


1
Pow-R-Line1a
30 Circuits, 100A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,100A, 3P BAB-H Main Breaker[Top Fed], Surface Mounted
Designations: 
SBL


1
Pow-R-Line3a
42 Circuits, 250A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 25k AIC,250A, Main Lugs Only[Top Fed], Surface Mounted
Designations: 
HP2


2
Pow-R-Line2a
42 Circuits, 100A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 14k AIC,100A, Main Lugs Only[Top Fed], Surface Mounted
Designations: 
HP3, HP4


1
Pow-R-Line1a
Multi-Section Panel:2 Sections, 84 Circuits, 225A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,225A, 3P EDB Main Breaker[Top Fed], Surface Mounted
Designations: 
LP2


2
Pow-R-Line1a
Multi-Section Panel:2 Sections, 84 Circuits, 225A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,150A, 3P EDB Main Breaker[Top Fed], Surface Mounted
Designations: 
LP3, LP4


1
Pow-R-Line3a
42 Circuits, 400A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 35k AIC,400A, Main Lugs Only[Top Fed], Surface Mounted
Designations: 
HP5


1
Pow-R-Line2a
42 Circuits, 225A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 14k AIC,225A, Main Lugs Only[Top Fed], Surface Mounted
Designations: 
HP5A


1
Pow-R-Line2a
42 Circuits, 225A, Fully Rated, 480Y/277V  3Ph  4W, Copper Bus, 14k AIC,225A, 3P FD Main Breaker[Top Fed], 110A, FDB  Sub-Feed Breaker, Surface Mounted
Designations: 
2HP1


1
Pow-R-Line1a
Multi-Section Panel:3 Sections, 126 Circuits, 225A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,225A, 3P EDB Main Breaker[Top Fed], Surface Mounted
Designations: 
2LP1


1
Pow-R-Line1a
Multi-Section Panel:2 Sections, 84 Circuits, 225A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,150A, 3P EDB Main Breaker[Top Fed], Surface Mounted
Designations: 
LP5


1
Pow-R-Line1a
42 Circuits, 225A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,110A, 3P EDB Main Breaker[Top Fed], Surface Mounted
Designations: 
LP5A


1
Pow-R-Line1a
Multi-Section Panel:2 Sections, 84 Circuits, 225A, Fully Rated, 208Y/120V  3Ph  4W, Copper Bus, 10k AIC,225A, 3P EDB Main Breaker[Top Fed], Surface Mounted
Designations: 
KP


1
PRLC Switchboard
Pow-R-Line C Switchboard, Front Access/ Front and Rear Align, Type 3R (nonwalk-in) Flat Roof
480Y/277V 3-Phase 4-Wire, 2500 Copper, Minimum Interrupt Rating: 65kA, Bus Bracing Rating: 65kA
1
Pow-R-Line C
3
Type 3R (nonwalk-in) Flat Roof
3
Heater Package - (CPT, heater, thermostat, fused disconnect)
2
Vertical Isol. Barrier (Service Entrance)
1
Horizontal Isol. Barrier (Service Entrance)
1
Service Entrance Label
1
2500 Amp CU Main Structure
1
2500A Utility Metering - NEMA (NEMA)
1
Digitrip RMS520 LSIG
14
Nameplate
1
Shunt Trip (100-127Vac/Vdc)
1
2500 Amp CU Bussed Incoming Pull Section
1
2500 Amp CU Distribution Structure
12
Thermal Mag Trip - Standard
1
Gutter Doors
1
CPS 400kA SPD with SuperVisor Diagnostic Package, (Disconnect Included)
1
MTST120V TEST KIT 
1
2500 A. Magnum DS Brkr MDS-630 [Fixed-Manual], Trip 2500 A., RMS520 LSIG
1
400A 3P [HKD 400A Frame], Trip 400 A., Thermal Mag
2
200A 3P [HFD 225A Frame], Trip 200 A., Thermal Mag
2
70A 3P [HFD 225A Frame], Trip 70 A., Thermal Mag
1
250A 3P [HJD 250A Frame], Trip 250 A., Thermal Mag
2
100A 3P [HFD 225A Frame], Trip 100 A., Thermal Mag
1
350A 3P [HKD 400A Frame], Trip 350 A., Thermal Mag
2
500A 3P [LGH 600A Frame], Trip 500 A., Thermal Mag
1
45A 3P [HFD 225A Frame], Trip 45 A., Thermal Mag
1
3P [HFD 225A Frame] Provision, Trip  A., 


Designations: 
SWBD


15
Safety Switches
DH361FGK,
BE31A, 600 VAC, 30 Amps, 3-Pole, Fusible with No Neutral, NEMA 1 Enclosure 
Designations: 



1
Safety Switches
DH261FGK,
BE31A, 600 VAC, 30 Amps, 2-Pole, Fusible with No Neutral, NEMA 1 Enclosure 
Designations: 



4
Safety Switches
DH361FRK,
BE31A, 600 VAC, 30 Amps, 3-Pole, Fusible with No Neutral, NEMA 3R Enclosure 
Designations: 



2
Safety Switches
DH362FRK,
BE31A, 600 VAC, 60 Amps, 3-Pole, Fusible with No Neutral, NEMA 3R Enclosure 
Designations: 



11
Safety Switches
DH222NGK,
BE31A, 240 VAC, 60 Amps, 2-Pole, Fusible with Neutral, NEMA 1 Enclosure 
Designations: 



1
Safety Switches
DH324NGK,
BE31B, 240 VAC, 200 Amps, 3-Pole, Fusible with Neutral, NEMA 1 Enclosure 
Designations: 



40
Manual Starters
MS MTR STA
Designations: 
MNL MS 1-POLE


3
Manual Starters
MTR SENT  A
Designations: 
MNL MS-1P N3R


43
NEMA MANUAL & DRUMS
MS HEATER A
Designations: 
HEATER



Total Quote Price:
$102,034.54
FUSES ARE NOT INCLUDED

NEMA 3R MST WILL NOT HAVE PILOT LIGHT. 

PANELBOARDS WILL NOT BE FURNISHED WITH SKIRTS 
ADDITIONAL WARRANTY PER SPEC. 16441-2 PART 1.4- 5 YEARS 

ADD $ 2000.00 FOR 5 YEAR WARRANTY OF PANELS AND SWITCHBOARD 

All orders must be released for manufacture within 90 days of date of order entry.  If approval drawings are required, drawings must be returned approved for release within 60 days of mailing.  If drawings are not returned accordingly, and/or if shipment is delayed for any reason, the price of the order will increase by 1.0% per month or fraction there of for the time the shipment is delayed.


