[image: image1.png]


554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net


August 28, 2013
William Efferson
Architect
Office of State Fire Marshal
8181 Independence Blvd.
Baton Rouge, LA  70806
Re:  
PO437655

Dear Mr. Efferson,
In regards to your review letter dated August 27, 2013 for the above referenced project.  In item 5 you reference 101:36.3.6 and IBC 1018.1 requiring that corridors be separated with a minimum one-hour rated construction.  However, as this building will be provided with an automatic sprinkler system the protected corridors are not required due to the following exceptions:
1. NFPA 101:36.3.6.1(3) Within buildings protected throughout by an approved, supervised automatic sprinkler system in accordance with 9.7.1.1(1).
2. IBC Table 1018.1 – Occupancy M - REQUIRED FIRE-RESISTANCE RATING (with sprinkler system) = 0 hours.

Please find attached a copy of your review letter dated August 27, 2013.  If you have any additional questions please do not hesitate to contact me.
Sincerely,
[image: image2.jpg]IDAMMON

ENGINEERING | NLC.

J  Archiltectls & Engineers





Kevin J. Kinchen
Chief Architect
Enclosures

Cc:
Dave Kaufmann

Farhad Aduli
