554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net

July 21, 2014

Ms. Wendy Ferrill, B.E.

c/o Mississippi State Department of Health

570 East Woodrow Wilson

Jackson, MS 39215-1700

Re:		Dreamland Mobile Home Park, Nicholson Water Association, PWS_ID# 0550041

Pearl River County, Ref #116069

Dear Ms. Ferrill,

In reference to your April 8, 2014 letter requesting clarification for the Dreamland Mobile Home Park Upgrade/Modification project, the following information is presented for your consideration.

- We have made a submittal to the Mississippi DEQ concerning the wastewater collection system and proposal to interconnect to the existing public permitted wastewater treatment facility (the Nicholson Sewerage District).  At this point we are awaiting their reply.  Upon receipt of their permit letter, it shall be forwarded to you (reference item #1 on your letter).

- A letter from the Nicholson Water & Sewer Association is enclosed indicating the future water & sewer interconnection with that agency (reference item #2 on your letter).

- We have made a submittal to the Pearl River County Utility Authority and await their reply.  Upon receipt of their letter acknowledging the project, it shall be forwarded to you (reference item #3 on your letter).

- Water mains and sewer mains shall be separated by 10’ horizontally and 18” vertically (water above sewer) when crossing.  This information shall and has been incorporated into the design plans and specifications sheets (reference item #4 on your letter).

- As discussed with the Nicholson Water Association, water samples shall be collected and submitted to the Mississippi State Department of Health for analysis and approval.   Disinfection shall be using a 50 mg/l free chlorine residual for a contact time for 24 hours. This information shall and has been incorporated into the design plans and specifications sheets (item #5 on your letter).

- A title page is included (reference item #6 on your letter).

- Enclosed are plans & specifications for the existing mobile home park site lots delineating the lot positions (I reference item #7 on your letter).

In essence, the requests listed on your April 8, 2014 letter are being honored.  The two outstanding items, letters from the Mississippi DEQ and the Pearl River County Utility Authority, shall be forwarded to you immediately upon receipt.

Should you have any questions, or if further information if required, please feel free to contact me.  A prompt reply is greatly appreciated.

Respectfully,

Brian A. Mistich, P.E.

Mississippi Registration #20971

Bill Kingsmill’s contact information is as follows:

William Kingsmill (kingsmillprop@bellsouth.net)

Cell: (504) 528 3838

1200 Business Highway 190, Suite 13

Covington, LA 70433

Lawrence Wm. Haik, Sr

Republic Commercial Properties, LLC

1539 Royal Palm Dr.

Slidell, LA 70458

(985) 960-7033