## Life-Safety Information
LIFE SAFETY INFORMATION
APPLICABLE CODES
NFPA 101 LIFE-SAFETY CODE 2009
OCCUPANCY TYPE(S) AND CHAPTER(S)
INDUSTRIAL (CHAPTER 40)
MULTIPLE, MIXED, OR SEPARATE OCCUPANCY |  | (REFERENCE CHAPTER 6)
N/A
CLASSIFICATION OF HAZARD OF CONTENTS
(REFERENCE: OCCUPANCY CHAPTER AND 6.2.2: SPECIFY LOW, ORDINARY, OR HIGH)
CONSTRUCTION TYPE(S) | (REFERENCE: CHAPTER8, TABLE A.8.2.1.2 AND COMMENTARY TABLE 8.1 IN HANDBOOK)
II(000)
MINIMUM CONSTRUCTION REQUIREMENTS |  | (REFERENCE OCCUPANCY CHAPTER)
APPLICABLE DEFINITIONS |  | (REFERENCE: CHAPTER 2)
N/A
OCCUPANCY
OCCUPANCY LOAD CALCULATIONS |  | (REFERENCE: TABLE 7.3.1.2)
FIRST FLOOR
OCC/FUNCTION OF SPACE | FLOOR AREA PER OCC (SF) X | ACTUAL SF | OCCUPANT LOAD
BUSINESS | 100 | 1,845 SF | 18
MEZZANINE | 100 | 1,845 SF | 18
|  | TOTAL | 37
INCIDENTAL USE AREAS AND REQUIRED SEPARATION
ROOM OR AREA |  | SEPARATION
N/A
MEANS OF EGRESS
NUMBER OF EXITS |  | (REFERENCE: OCCUPANCY CHAPTER AND TABLE A.7.6)
2
MINIMUM EXIT SEPARATION DISTANCE FOR REMOTELY LOCATED EXITS
(REFERENCE: SECTION 7.5; SPECIFY 1/2 OR 1/3 DIAGONAL DISTANCE OF AREA SERVED)
1/3 DIAGONAL = | 25'-2"
MAXIMUM DEAD-END CORRIDORS |  | (REFERENCE: OCCUPANCY CHAPTER AND TABLE A.7.6)
50'
MAXIMUM COMMON PATH OF TRAVEL DISTANCE |  | (REFERENCE: OCCUPANCY CHAPTER AND TABLE A.7.6)
75'
MAXIMUM TRAVEL DISTANCE TO EXITS |  | (REFERENCE: OCCUPANCY CHAPTER AND TABLE A.7.6)
150'
AREA OF REFUGE REQUIREMENTS |  | (REFERENCE: OCCUPANCY CHAPTER AND TABLE A.7.2.12)
N/A
CORRIDOR OR PASSAGEWAY WIDTH REQUIREMENTS
(REFERENCE: OCCUPANCY CHAPTER, TABLE 7.2.2.2.1.1(A) OR (B), AND TABLE 7.2.2.2.1.2(B))
N/A
STAIR WIDTH REQUIREMENTS
(REFERENCE: OCCUPANCY CHAPTER, TABLE 7.2.2.2.1.1(A) OR (B), AND TABLE 7.2.2.2.1.2(B))
44"
ACCESSIBILITY REQUIREMENTS FOR EGRESS COMPONENTS |  |  | (7.5.4)
N/A
CAPACITY OF MEANS OF EGRESS |  | (REFERENCE: 7.3 AND TABLE 7.3.3.1)
COMPONENT | OCCUPANT LOAD | X CAPACITY FACTOR | MINIMUM WIDTH
EXITS | 19 | 0.2 | 4"
*MAIN ENTRANCE MUST BE SIGNED TO ACCOMODATE 1/2 OCCUPANT LOAD OF BUILDING
FIRE RESISTANCE RATING REQUIREMENTS
CHAPTER 8
EXTERIOR BEARING WALLS |  | (REFERENCE TABLE A.8.2.1.2 | 0 HOURS
INTERIOR BEARING WALLS |  | (REFERENCE TABLE A.8.2.1.2) | 0 HOURS
COLUMNS |  | (REFERENCE TABLE A.8.2.1.2) | 0 HOURS
BEAMS, GIRDERS, TRUSSES, AND ARCHES |  | (REFERENCE TABLE A.8.2.1.2) | 0 HOURS
FLOOR-CEILING ASSEMBLIES |  | (REFERENCE TABLE A.8.2.1.2) | 0 HOURS
ROOF-CEILING ASSEMBLIES |  | (REFERENCE TABLE A.8.2.1.2) | 0 HOURS
INTERIOR NON-BEARING WALLS |  | (REFERENCE TABLE A.8.2.1.2) | 0 HOURS
EXTERIOR NON-BEARING WALLS |  | (REFERENCE TABLE A.8.2.1.2) | 0 HOURS
SHAFT ENCLOSURE |  | (SECTION 8.6.5) | 0 HOURS
EXIT ENCLOSURE |  |  | 1 HOUR
EXIT PASSAGEWAY / EXIT ACCESS CORRIDORS |  |  | N/A
HORIZONTAL EXIT |  |  | 2 HOURS
ATRIUMS |  |  | N/A
MEZZANINES
CONCEALED SPACES AND DRAFTSTOPS |  |  | N/A
STORAGE, BOILER, OR FURNACE ROOMS |  |  | N/A
COMMUNICATING SPACES |  | (SECTION 8.6.6) | N/A
OPENING PROTECTIVES |  | (CHAPTER 8, TABLE 8.3.4.2)
COMPONENT | WALLS & PART FIRE RATING (HR) | FIRE DOOR ASSEMBLIES | FIRE WINDOW ASSEMBLIES (HR)
ELEVATOR | 1 HR | 1 HR | 1 HR
STAIRWAYS | 1 HR | 1 HR | 1 HR
SMOKE BARRIERS | 1 HR | 1/3 HR | 1/3 HR
ADDITIONAL CODE REQUIREMENTS |  | (OCCUPANCY CHAPTER 36)
EXTINGUISHMENT REQUIREMENTS |  | SPRINKLER (REQUIRED)
SUBDIVISION OF BUILDING SPACE |  | N/A
DETECTION, ALARM, AND COMMUNICATION SYSTEMS |  | YES
EMERGENCY LIGHTING |  | PER 38.2.6
SPECIAL PROVISIONS - STAGES & PLATFORMS |  | N/A
OTHER |  | N/A
EMERGENCY LIGHTING |  | PER 38.2.11.2
ALLOWABLE HEIGHT AND BUILDING AREA |  | PER IBC EQUIVALENT CONSTRUCTION TYPE
CONSTRUCTION TYPE (NFPA) |  | II(000)
CONSTRUCTION TYPE (IBC) |  | IIB (UNLIMITED AREA BUILDING - SECTION 507)
MAXIMUM HEIGHT IN STORIES | (REFERENCE: IBC TABLE 503) | 1 PER IBC SECTION 507
MAXIMUM HEIGHT IN FEET | (REFERENCE: IBC TABLE 503) | N/A
MAXIMUM AREA IN SQUARE FEET | (REFERENCE: IBC TABLE 503) | IIB (UNLIMITED AREA BUILDING - SECTION 507)