Background:

This document contains the load calculation for the Dollar General store located at 2440 Highway 190 West,  70460.  It is unlikely that the Heat and the Air Conditioner will be used at the same time, so Calculations were prepared assuming the A/C system running, then with the Heat system running.

The power supply is as follows:  400A, 240V, 3 Phase, 4 Wire Delta High Leg.

Calculations for the Air Conditioning Load:

Load for building minus the HVAC system is as follows:

Phase A:  		24325 KVA  	=  	203A

Phase B:		0

Phase C:		22825 KVA 	=	190A

Nameplate data for the existing Air Conditioning is as follows:

Unit 1:		16600 KVA 	=	46 A

Unit 2:		18000 KVA	=	50 A

--------------------------------------------------

Existing A/C Load: 	34600 KVA	=	96 A

(11533 KVA per phase)

Total Load of the existing building plus the existing A/C load:

Phase A:  		35858 KVA  	=  	299A

Phase B:		11533		=	96 A

Phase C:		34358 KVA 	=	286A

Nameplate data for the new A/C load:

Unit 3 Condenser:			7056 KVA 	=	29.4 A

Unit 3 Evaporator:		3240 KVA	=	13.5 A

Unit 4 Condenser:			7056 KVA 	=	29.4 A

Unit 4 Evaporator:		 3240 KVA	=	13.5 A

--------------------------------------------------

New  A/C: 				20592 KVA	=	85.8 A

(10296 KVA per phase A & C)

Total load with the new Air Conditioner:

Phase A:  		46154 KVA  	=  	385 A

Phase B:		11533 KVA	=	96 A

Phase C:		44654 KVA 	=	372 A

Calculations for the Heater Load:

Load for building minus the HVAC system is as follows:

Phase A:  		24325 KVA  	=  	203A

Phase B:		0

Phase C:		22825 KVA 	=	190A

The Nameplate data for the existing heater is as follows:

Unit 1:		30000 KVA 	=	83.3 A

Unit 2:		27000 KVA	=	75 A

--------------------------------------------------

Total  Heat: 		57600 KVA	=	158.3 A

(19200 KVA per phase)

Total Load of the existing building plus the heater:

Phase A:  		43525 KVA  	=  	361A

Phase B:		19200 KVA	=	158A

Phase C:		42025 KVA 	=	348A

Nameplate data for the new heater load:

Unit 3 Heater:				20000 KVA 	=	83.3 A

Unit 3 Air Handler:		3240 KVA	=	13.5 A

Unit 4 Condenser:			20000 KVA 	=	83.3 A

Unit 4 Air Handler:		 3240 KVA	=	13.5 A

--------------------------------------------------

New  Heater: 				46480 KVA	=	194 A

(23240 KVA per phase A & C)

Total load with the new Heater:

Phase A:  		66765 KVA  	=  	555 A

Phase B:		19200 KVA	=	160 A

Phase C:		65265 KVA 	=	542 A

Conclusion:

The existing power system will handle the additional Air Conditioning load but will be close to capacity.

The technician took a current reading on phases A & C with a clamp on ammeter and read the following values 110A and 88A respectively.   The readings were taken during  the summer, with the Air Conditioner on.  The ammeter readings were considered to establish the recommendation.

The existing power system will not handle the additional heater load.

Recommendation:

Recommend specifying 3 phase A/C  units.  This will distribute the power across all 3 phases and as a result, lower the ampacity.

If a 3 Phase units are not available, the new A/C units can be connected as follows:

Connect one unit to phases A and B and the other unit to Phases B and C.

This will distribute some of the load to the B phase.

Installing the 20KW Heat Kits is not recommended.

Prepared by:

Anthony Ponceti

Electrical Designer

Dammon Engineering