## Table1
DIRECTORY | WATTS LOAD |  |  | CKT NO. | AMPS |  | AMPS | CKT NO. | WATTS LOAD |  |  | DIRECTORY
| L1 | L2 | L3 | [5 empty] | L1 | L2 | L3
Lighting | 800 |  |  | 1 | 20 |  | 100 |  | 10000 |  |  | HVAC Heat = 30 KW A/C = 16.6 KVA
High Voltage | [7 empty] | 2 |  | 10000
Lighting rows 3 & 4 |  |  | 800 | 3 | 20 | [5 empty] | 10000
Lighting | 800 |  |  | 5 | 20 |  | 100 |  | 9000 |  |  | HVAC Heat = 27 KW A/C = 18.0 KVA
High Voltage | [7 empty] | 4 |  | 9000
Lighting rows 9 & 10 |  |  | 800 | 7 | 20 | [5 empty] | 9000
Lighting | 800 |  |  | 9 | 20 |  | 20 | 6 | 500 |  |  | Power
High Voltage | [11 empty] | High Voltage
Lighting |  |  | 800 | 11 | 20 |  | 20 | 8 |  |  | 500 | Power
Lighting Right | 800 |  |  | 13 | 20 |  | 20 | 10 | 500 |  |  | Power
High Voltage | [11 empty] | High Voltage
Lighting |  |  | 800 | 15 | 20 |  | 20 | 12 |  |  | 500 | Power
Lighting | 800 |  |  | 17 | 20 |  | 20 | 14 | 400 |  |  | Night Light
High Voltage | [11 empty] | High Voltage
Lighting row 13 Cooler Side |  |  | 800 | 19 | 20 |  | 20 | 16 |  |  | 500 | Power
Lighting row 7 & 8 | 800 |  |  | 21 | 20 |  | 20 | 18 | 500 |  |  | Power Pole Reg
High Voltage | [11 empty] | High Voltage
Sub Panel P3 to the Right |  |  | 5725 | 23 | 100 |  | 100 | 20 |  |  | 10300 | Sub Panel to the Left
| 5725 |  |  | 25 |  |  |  | 22 | 11900
High Voltage | [11 empty] | High Voltage
Lighting row 1 & 2 |  |  | 800 | 27 | 20 |  | 20 | 24 |  |  | 500 | Power Reg
SUBTOTAL | 10525 | 0 | 10525 | [5 empty] | 32800 | 19000 | 31300 | SUBTOTAL
VOLTAGE: 240/120 PHASE: 3 WIRE: 4 DELTA HIGH LEG | [5 empty] | TOTAL WATTS, L1 |  |  | 43325 | PANEL NO. |  | MP1
MAIN BREAKER: YES FRAME: 400 AMP - TRIP: 400 AMP | [5 empty] | TOTAL WATTS, L2 |  |  | 19000
MAIN BUS: 400 AMP NTL BUS: YES GND BUS: YES | [5 empty] | TOTAL WATTS, L3 |  |  | 41825 | LOCATION |  | Storage Room
MANUFACTURER: SIEMENS | MODEL: P1 |  |  |  | MFG DATE: 2004 | TOTAL WATTS |  |  | 104150
NOTES: FED FROM UTILITY, DELTA HIGH LEG | [5 empty] | MOUNTING: SURFACE