## Sheet1
| Project | HVAC Heat Load Calculations for Seaux Polished
| Date | 2019-02-20
| Zone #1 | Nail Salon |  |  |  | (Sensible Heat Loads)
| Zone Specs |  | 500 | s.f. total area for Zone 1
| 0 | s.f. North Shaded Single Pane Glass
| 0 | s.f. North Shaded Double Pane Glass
| 0 | s.f. North Shaded Triple Pane Glass
| 0 | s.f. NorthEast or NorthWest Single Pane Glass
| 0 | s.f. NorthEast or NorthWest Double Pane Glass
| 0 | s.f. NorthEast or NorthWest Triple Pane Glass
| 0 | s.f. East/West Single Pane Glass
| 170 | s.f. East/West Double Pane Glass
| 0 | s.f. East/West Triple Pane Glass
| 0 | s.f. SouthEast or SouthWest Single Pane Glass
| 0 | s.f. SouthEast or SouthWest Double Pane Glass
| 0 | s.f. SouthEast or SouthWest Triple Pane Glass
| 0 | s.f. South Single Pane Glass
| 0 | s.f. South Double Pane Glass
| 0 | s.f. South Triple Pane Glass
| 21 | s.f. Single Pane Exterior Doors
s.f. Double Pane Exterior Doors
s.f. Triple Pane Exterior Doors
| Sensible BTUh Gain for North Shaded Single Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for North Shaded Double Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for North Shaded Triple Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for NorthEast or NorthWest Single Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for NorthEast or NorthWest Double Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for NorthEast or NorthWest Triple Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for East/West Single Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for East/West Double Pane Glass | [6 empty] | 16150 | BTUh
| Sensible BTUh Gain for East/West Triple Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for SouthEast or SouthWest Single Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for SouthEast or SouthWest Double Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for SouthEast or SouthWest Triple Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for South Single Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for South Double Pane Glass | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for South Triple Pane Glass | [6 empty] | 0 | BTUh
BTUh
| Sensible BTUh Gain for Single Pane Exterior Doors | [6 empty] | 277.2 | BTUh
| Sensible BTUh Gain for Double Pane Exterior Doors | [6 empty] | 0 | BTUh
| Sensible BTUh Gain for Triple Pane Exterior Doors | [6 empty] | 0 | BTUh
| Glass total BTUh gain = | [6 empty] | 16427.2 | BTUh
********************************************************************
Zone 1 area with walls demising to non-temperature controled areas
|  |  | 200 | s.f. Exterior CMU wall, R-5 insulation
|  |  | 0 | s.f. of inside demising wall to next door tennant space, no insulation
| Sensible BTUh Gain for Exterior CMU wall = | [6 empty] | 620 | BTUh
| Sensible BTUh Gain for interior demising wall = | [6 empty] | 0 | BTUh
| Wall Heat Gain total = | [6 empty] | 620 | BTUh
********************************************************************
Zone 1 area Ceiling Factor
| Sensible BTUh Gain for Ceiling R-19 Insulation | [6 empty] | 2600 | BTUh
********************************************************************
| 16.6667 | Estimate on number of occupants to account for Sensible Heat Load
| Sensible BTUh Gain for People = | [6 empty] | 3750 | BTUh
********************************************************************
Sensible BTUh Gain for Appliances:
| Coffee brewer/warmer | [5 empty] | 0 | BTUh
| Computer Terminal | [5 empty] | 0 | BTUh
| Cold Drink | [5 empty] | 0 | BTUh
| Hot Drink | [5 empty] | 0 | BTUh
| Refrigerator | [5 empty] | 0 | BTUh
| Sensible BTUh Gain for Appliances : | [6 empty] | 0 | BTUh
********************************************************************
Square Feet of Ducts Running Outside Conditioned Spaces Factors.
| 0 | s.f. of duct outside of conditioned space
| Sensible BTUh Gain for Ducts Out of Conditioned Spaces = | [6 empty] | 0 | BTUh
********************************************************************
| Sensible BTUh Gain for for Lighting = | [6 empty] | 1500 | BTUh
********************************************************************
| Zone 1 total Sensible Heat Loads, BTUh = | [6 empty] | 24897.2 | BTUh
********************************************************************
********************************************************************
| Zone #1 | Nail Salon |  |  |  | (Latent Heat Loads)
********************************************************************
Fresh air requirements:
Az | 500 | s.f. - | 15 | % Non Occupiable floor area = |  |  |  | 425 | s.f. Occupiable Floor Area
Pz | 425 | s.f. | 25 | Occupants per |  | 1000 | s.f. = | 10.625 | Occupants
Rp | 20 | from Table 403.3.1.1
Ra | 0.12 | from Table 403.3.1.1
| Formula = | Vbz = RpPz + RaAz = |  | 263.5 | cfm required fresh air
| Salons also have a minimum exhaust airflow rate = |  |  |  |  | 0.6 | cfm/ft2 = | 300 | cfm exhaust
Table 403.3.1.1 note h states that nail salons shall exhaust 50 cfm per manicure and pedicure stations
This nail salon expects 2 ea manicure and 2 each pedicure stations therefore a minimum exhaust for these
| stations = | 4 x 50 cfm = | 200 | cfm exhaust
The note also states that this exhaust system shall be permitted to be applied to the exhaust flow rate for Salons
above when this exhaust system is operated continuously. Therefore the stations will exhaust a total of:
| 300 | cfm exhaust which also means it will draw this much fresh air from outside sources.
BTUh gain for Fresh Air; 97 Deg outside temp, 72 Deg inside temp; 97% Humidity
| 97 | Degree Outside | 75 | Degree Inside | = | 22 | tRise
| 97 | % Humidity changes Load Factor = |  |  |  | 1.1
| The volume of Zone 1 = | [5 empty] | 5000 | ft3
| 0.6 | ACH from Building results in cfm = |  |  |  |  | 50 | cfm
| The traffic rate estimated through the single door = | [5 empty] | 0 | Entrances / hr
|  | Door infiltration estimated = |  |  |  | 10 | cfm | Total Infiltration = |  | 60 | cfm
| Total amount of outside air to cool |  |  |  | 300 | cfm but requires supplemental air from other sources
[5 empty] | 240 | cfm from other sources than infiltration
cfm x Load Factor (where Normal Humidity = 1.08) x tRise = BTUh
[8 empty] | 7260 | BTUh
********************************************************************
| 10.625 | Estimate on number of occupants to account for Sensible Heat Load
| Latent BTUh Gain for People = | [6 empty] | 3453.125 | BTUh
********************************************************************
Latent BTUh Gain for Appliances:
| Coffee brewer/warmer | [5 empty] | 0 | BTUh
| Hot Drink | [5 empty] | 0 | BTUh
| Appliance BTUh Gain = | [6 empty] | 0 | BTUh
********************************************************************
| Zone 1 total Latent Heat Loads, BTUh = | [6 empty] | 10713.125 | BTUh
********************************************************************
| Zone 1 Estimate Tonnage of HVAC = | [5 empty] | 2.9675 | tons hvac
********************************************************************
********************************************************************
********************************************************************
********************************************************************