4. Air Testing 
a. Each section of new CIPP liner shall be tested between successive manholes by plugging and bracing all openings in the pipe and the upper ends of all service laterals. Prior to insertion in the sewer, each plug shall be checked with a soap solution to detect any air leakage.  If any leaks are found, the air pressure shall be released and the leaks eliminated or the plug replaced. 
b. The test of the pipe and service laterals shall be conducted in the presence of the Engineer. Testing of pipe shall be performed in accordance with the latest version of ASTM F-1417. 
c. It is the Contractor’s responsibility to have the pipe clean and to determine the ground water level prior to testing the pipe. 
d. Air pressure in the sewer shall be slowly increased to 4.0 psi above groundwater pressure (1.0 psi for each 2.3 feet of water elevation above the highest point of the pipe). Do not allow the air pressure at any point in the pipe to reach 9.0 psi under any circumstances. Allow the pressure to stabilize for 5 minutes, then reduce the pressure to 3.5 psi above groundwater pressure and start the test. Stop the air release and record the decrease in pressure over time. 
e. The time taken for the pressure to decrease from 3.5 to 2.5 psi above groundwater pressure shall be equal to or greater than the time below.

Pipe Diameter (in.) Minimum Time Lapse (min:sec) 
      100 ft 	150ft 	200 ft 	250 ft 	300 ft 	350 ft 	400 ft 	450 ft 
8    7:34 	7:34 	7:34 	7:34 	7:36 	8:52 	10:08 	11:24 
10   9:26 	9:26 	9:26 	9:53 	11:52 	13:51 	15:49 	17:48 
12  11:20 	11:20 	11:24 	14:15 	17:05 	19:56 	22:47 	25:38 
  
f. The time for the pressure to fall from 3.5 to 2.5 psi, both above groundwater pressure, shall no be less than 10 seconds regardless of pipe diameter. 
g. If the time is less than the allowable time, the pipe will be considered defective and shall be repaired and re-tested at no additional cost to the Board. 
h. Safety Provisions: Securely brace the plugs used to close the sewer pipe for the air test in order to prevent the unintentional release of a plug, which can become a high velocity projectile. Locate gauges, air piping manifolds, and valves at the top of the ground. No one shall be  permitted to enter a manhole where a plugged pipe is under pressure 4 pounds (gauge) air pressure develops a force against the plug in a 12-inch diameter pipe of approximately 450 pounds. Provide a safety release device set to release at 10 psi between the air supply and the 
sewer under test. 
i. Regardless of the outcome of any test, repair any noticeable leak.