Reline America CIPP is not suitable for laterals

----------------------------------------------------------------------------------------------------------

7/8/2013  Talked with BLD Services, Insituform spun off the service laterals to BLD.

TV inspection,  $500 setup fee per MH segment where laterals connect.  Plus $450 per lateral. Approx. $9000

Estimating the cost of lining service laterals.  $3500 for a 50ft to 60ft service lateral and $50/ft after that.  Runs longer than 150ft shall need a two-way wye cleanout to allow for pulling the liner.  Any length longer does not allow for the materials to be mixed on site and placed in lateral then allowed to cure.  BLD uses a air drying compound without additional heat.  Typical setup, with cure time and putting lateral back to service approximately 2.5 hours.

Estimating Repairs of laterals before lining:  Bid was $563,200 and 60% of that was for hand digging.  Therefore estimate repairs to include $168/ft to hand dig plus $20/ft for installation. ($188/ft)

If a lateral passes within 10 feet of the base of a tree expect to replace 10 feet of lateral.

If a lateral passes within 20 feet of the base of a tree expect to replace 5 feet of lateral.

To install a clean-out estimate digging 5 feet of lateral.