SECTION 22 13 43 - FACILITY PACKAGED SEWAGE PUMPING STATIONS

PART 1	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced.	The publications are referred to within the text by the basic designation only.

AMERICAN WATER WORKS ASSOCIATION (AWWA)

AWWA C104/A21.4	(2003) Cement-Mortar Lining for

Ductile-Iron Pipe and Fittings for Water

AWWA C110/A21.10	(2008) Ductile-Iron and Gray-Iron Fittings for Water

AWWA C111/A21.11	(2000) Rubber-Gasket Joints for

Ductile-Iron Pressure Pipe and Fittings

AWWA C115/A21.15	(2005) Flanged Ductile-Iron Pipe With

Ductile-Iron or Gray-Iron Threaded Flanges

AWWA C151/A21.51	(2002; Errata 2002) Ductile-Iron Pipe, Centrifugally Cast, for Water

AWWA C500	(2002; R 2003) Metal-Seated Gate Valves for Water Supply Service

AWWA C509	(2001) Resilient-Seated Gate Valves for

Water Supply Service

AWWA C600	(2005) Installation of Ductile-Iron Water

Mains and Their Appurtenances

AWWA M23	(2002) Manual: PVC Pipe - Design and

Installation

ASME INTERNATIONAL (ASME)

ASME B1.20.1	(1983; R 2006) Pipe Threads, General

Purpose (Inch)

ASME B16.1	(2005) Standard for Gray Iron Threaded

Fittings; Classes 125 and 250

ASME B16.11	(2005) Forged Fittings, Socket-Welding and

Threaded

ASME B16.3	(2006) Malleable Iron Threaded Fittings, Classes 150 and 300

ASME B31.3	(2008) Process Piping

ASTM INTERNATIONAL (ASTM)

ASTM A 123/A 123M	(2008) Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

ASTM A 126                      	(2004) Standard Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings

ASTM A 53/A 53M	(2007) Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

ASTM A 536	(1984e1; R 2004) Standard Specification for Ductile Iron Castings

ASTM D 1784	(2008) Standard Specification for Rigid Poly(Vinyl Chloride) (PVC) Compounds and Chlorinated Poly(Vinyl Chloride) (CPVC) Compounds

ASTM D 1785	(2006) Standard Specification for Poly(Vinyl Chloride) (PVC), Plastic Pipe, Schedules 40, 80, and 120

ASTM D 2241	(2005) Standard Specification for Poly(Vinyl Chloride) (PVC) Pressure-Rated Pipe (SDR Series)

ASTM D 2464	(2006) Standard Specification for Threaded Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80

ASTM D 2466	(2006) Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40

ASTM D 2467	(2006) Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80

ASTM D 3139	(1998; R 2005) Joints for Plastic Pressure

Pipes Using Flexible Elastomeric Seals

ASTM F 477	(2008) Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA MG 1	(2007; Errata 2008) Standard for Motors and Generators

1.2	DESCRIPTION OF WORK

The work includes providing submersible sewage grinder pump station and related work.	Provide system complete and ready for operations.  Grinder pump station system including equipment, materials, installation, and workmanship as specified herein.

1.3	SUBMITTALS

A.	Submit in accordance with Section 01 33 00, SUBMITTAL PROCEDURES.

B.	Manufacturer's Literature and Data:

1.  Pump:

a.  Manufacturer and model.

b.  Operating speed.

c.  Capacity.

d.  Characteristic performance curves.

2.  Motor:

a.  Manufacturer.

b.  Speed.

c.  Current Characteristics and W (HP).

d.  Efficiency

C.	Certified copies of all the factory and construction site test data sheets and reports.

D.  	Complete operating and maintenance manuals including wiring diagrams, technical data sheets and information for ordering replaceable parts:

1.  Include complete list indicating all components of the system.

2.  Include complete diagrams of the internal wiring for each item of equipment.

3.  Diagrams shall have their terminals identified to facilitate installation, operating and maintenance.

1.4	DELIVERY, STORAGE, AND HANDLING OF MATERIALS

1.4.1	Delivery and Storage

Inspect materials delivered to site for damage.  Unload and store with minimum handling.  Store materials in enclosures or under protective covering.  Store rubber gaskets not to be installed immediately under cover, out of direct sunlight.  Do not store materials directly on the ground.  Keep interior of pipes and fittings free of dirt and debris.

1.4.2	Handling

Handle pipe, fittings, valves, and other accessories in such manner as to ensure delivery to the trench in sound, undamaged condition.  Avoid injury to coatings and linings on pipe and fittings; make satisfactory repairs if coatings or linings are damaged.  Carry pipe to the trench; do not drag it.

1.5	EXCAVATION, TRENCHING, AND BACKFILLING

Provide in accordance with Section 31 00 00 EARTHWORK.

PART 2	PRODUCTS

2.1	PIPE AND FITTINGS

Provide pressure piping, air release valves, and related accessories for force main piping outside the sewage wet well in accordance with Section 33 30 00 SANITARY SEWERS.

2.1.1	Ductile-Iron Pipe

AWWA C151/A21.51, thickness Class 52.

2.1.1.1	Flanged Pipe

AWWA C115/A21.15, ductile iron.

2.1.1.2	Fittings

AWWA C110/A21.10, flanged.  Provide flanged joint fittings within wet well as indicated.  Provide mechanical joint fittings outside enclosure as indicated.  Use fittings with pressure rating at least equivalent to that of the pipe.

2.1.1.3	Joints

AWWA C115/A21.15 for flanged joints.  Use bolts, nuts, and gaskets for flanged connections recommended in the Appendix to AWWA C115/A21.15. Flange for setscrewed flanges must be of ductile iron, ASTM A 536, Grade 65-45-12, conforming to the applicable requirements of ASME B16.1, Class 250.  Setscrews for setscrewed flanges must be 190,000 psi tensile strength, heat treated, and zinc-coated steel.  Conform to the applicable requirements for mechanical-joint gaskets specified in AWWA C111/A21.11for setscrewed flange gaskets.  Use setscrewed gasket designed to provide for confinement and compression of gasket when joint to adjoining flange is

made.

2.1.2	PVC Plastic Pressure Pipe and Associated Fittings

2.1.2.1	Pipe and Fittings Less Than 4 inch Diameter

Use pipe, couplings and fittings manufactured of materials conforming to

ASTM D 1784, Class 12454-B.

(1)	Push-On Joint:	ASTM D 3139, with ASTM F 477 gaskets.	Fittings for push-on joints: AWWA C110/A21.10 or AWWA C111/A21.11.	Iron fittings and specials: cement-mortar lined (standard thickness) in accordance with AWWA C104/A21.4.

(2)		Solvent Cement Joint: Use pipe conforming to dimensional requirements of	ASTM D 1785 or ASTM D 2241 with joints meeting

the requirements of 150 psi working pressure and 200 psi hydrostatic test pressure.  Use fittings for solvent cement jointing conforming to ASTM D 2466 or ASTM D 2467.

2.1.3	Insulating Joints

Provide between pipes of dissimilar metals a rubber gasket or other approved type of insulating joint or dielectric coupling to effectively prevent metal-to-metal contact between adjacent sections of piping.

2.1.4	Accessories

Provide flanges, connecting pieces, transition glands, transition sleeves, and other adapters as required.

2.1.5	Flexible Flanged Coupling

Provide flexible flanged coupling applicable for sewage as indicated.  Use flexible flanged coupling designed for a working pressure of 350 psi.

2.2	VALVES AND OTHER PIPING ACCESSORIES

2.2.1	Gate Valves

Conform to AWWA C500 for valves with outside-screw-and-yoke rising-stem type with double disc gates and flanged ends.	Conform to AWWA C509 for valves with outside-screw-and-yoke rising-stem type with flanged ends. Provide valves with handwheels that open by counterclockwise rotation of the valve stem.  Bolt and construct stuffing boxes to permit easy removal of parts for repair.  Use valves from one manufacturer.

2.2.2	Check Valves Less Than 4 Inch Diameter

Neoprene ball check valve with integral hydraulic sealing flange, designed for a hydraulic working pressure of 175 psi.

2.2.3	Miscellaneous Metals

Use stainless steel bolts, nuts, washers, anchors, and supports for installation of equipment.

2.2.4	Quick Disconnect System with Hydraulic Sealing Flange

Use quick disconnect system consisting of a steel base plate for supporting the pumps, a hydraulic sealing flange, pump guide rails and the discharge pipe supports.  Use two guide rails of galvanized steel in accordance with ASTM A 123/A 123M.  Provide a steel lifting chain for raising and lowering the pump in the basin.  Build guides onto pump housing to fit the guide

post to assure perfect alignment between pump and guide rails.

2.2.5	Wet Well Vent

Galvanized ASTM A 53/A 53M pipe with insect screening.

2.3	SUBMERSIBLE SEWAGE GRINDER PUMPS

Provide submersible sewage pumps with grinder units and integral check valve as shown on the drawings.  Provide submersible, centrifugal sewage pumps and grinder units capable of grinding all materials found in normal domestic sewage, including plastics, rubber, sanitary napkins, disposable diapers, and wooden articles into a finely ground slurry with particle dimensions no greater than 1/4 inch.  Pump capacity and motor characteristics as indicated. Design pump to operate in a submerged or partially submerged condition.   Provide an integral sliding guide bracket and two guide bars capable of supporting the entire weight of the pumping unit.

2.4	PUMP MOTOR

Provide submersible sewage pumps in wet well NEMA MG 1, 3750 RPM, 240 volt, 1 phase, and 60 Hz cycle and for submersible pumps.  Motor horsepower must be not less than pump horsepower at any point on the pump performance curve.  Fit motors with lifting "eyes" capable of supporting entire weight of pump and motor.

2.5	PUMP CONTROL SYSTEM

Provide a sealed mercury float switch control system as indicated.  Provide floats, supports, and alarm.  Metal parts, if used, must be of bronze or equivalent corrosion resistant material.

2.5.1	Float Assembly Description

Use a direct acting float switch consisting of a normally-open mercury switch enclosed in a float.  Use pipe mounted float assembly.	  Use float molded of rigid high-density polyurethane foam, color-coded and coated with a durable, water and corrosion-resistant jacket of clear urethane.  Provide connecting cable and support pole in accordance with manufacturers recommendations.

2.5.2	Sewage Pump Alarm and Control Panel

Enclosed alarm panel in NEMA IV enclosure with a flashing red light and power present light with long life bulb in lockable enclosure.  Use panel switch power on light, push to test button for light and push to silence button for light with automatic reset for next alarm.  Use alarm designed to activate under the following conditions:

a.	High liquid level as sensed by float switch.

2.5.3	Electrical Requirements

Furnish motors with their respective pieces of equipment.  Furnish internal wiring for components of packaged equipment as an integral part of the equipment.  Provide power wiring and conduit for field installed equipment.

2.5.4	Electric Motor

Use hermetically sealed electric motor.  Seal the power cable inside the motor end bell.

2.6	UNDERGROUND EQUIPMENT ENCLOSURE

2.6.1	Access Hatch Cover

Provide access hatch cover as per manufacturer specification.  Use access hatch cover capable of withstanding a live load of 300 lbs./sq. ft.  Provide access cover security.

2.6.2	Wet Well

Provide basin with inside diameter as indicated.

2.6.3	Wet Well Base Material

Provide crushed stone as indicated on drawings.

PART 3	EXECUTION

3.1	INSTALLATION

Provide pump station in accordance with drawings and requirements of the respective equipment manufacturers.  Dampen and isolate equipment vibration.

3.1.1	Installation of PVC Plastic Pressure Pipe and Fittings

Unless otherwise specified, install pipe and fittings in accordance with paragraph entitled "General Requirements for Installation of Pipelines" of this section and with the recommendations for pipe joint assembly and appurtenance installation in AWWA M23, Chapter 7, "Installation."

a.	Pipe Less than 4 Inch Diameter:

(1) Make threaded joints by wrapping the male threads with joint tape or by applying an approved thread lubricant, than threading the joining members together.  Tighten joints with strap wrenches that will not damage the pipe and fittings.  Do not tighten joint more than 2 threads past hand-tight.

(2) Push-On Joints:  Bevel ends of pipe for push-on joints to facilitate assembly.  Mark pipe to indicate when the pipe is fully seated.  Lubricate gasket to prevent displacement. Exercise care to ensure that the gasket remains in proper position in the bell or coupling while making the joint.

(3) Solvent-weld joints: comply with the manufacturer's instructions.

3.1.2	Valves

Installation of Valves: Install gate valves conforming to AWWA C500 in accordance with AWWA C600 for valve-and-fitting installation and with the recommendations of the Appendix ("Installation, Operation, and Maintenance of Gate Valves") to AWWA C500.  Install gate valves conforming to AWWA C509 in accordance with AWWA C600 for valve-and-fitting installation and with the recommendations of the Appendix ("Installation, Operation, and Maintenance of Gate Valves") to AWWA C509.  Install check valves in accordance with the applicable requirements of AWWA C600 for valve-and-fitting installation, except as otherwise indicated.  Make and assemble joints to gate valves and check valves as specified for making and assembling the same type joints between pipe and fittings.

3.1.3	Steel Piping

Install steel piping in accordance with ASME B31.3.  Use PTFE pipe thread paste or PTFE powder and oil for jointing compound for pipe threads.

3.1.4	Force Main

Provide in accordance with Section 33 30 00 SANITARY SEWERS.

3.1.5	Equipment Installation

Install equipment in accordance with these specifications and the manufacturer's installation instructions.  Grout equipment mounted on concrete foundations before installing piping.  Install piping to avoid imposing stress on any equipment.  Match flanges accurately before securing bolts.

3.2	FIELD TESTS AND INSPECTIONS

Perform all field tests, and provide all labor, equipment, and incidentals required for testing, except that water and electric power needed for field tests will be furnished as set forth in Division 01.  Produce evidence, when required, that any item of work has been constructed in accordance with contract requirements.  Allow concrete to cure a minimum of 5 days before testing any section of piping where concrete thrust blocks have been provided.

3.2.1	Testing Procedure

Test piping in accordance with the Section 33 30 00 SANITARY SEWERS.  Test in operation all equipment to demonstrate compliance with the contract requirements.

3.2.2	Sewage Grinder Pump Lift Station

Test pumps and controls, in operation, under design conditions to insure proper operation of all equipment.  Provide all appliances, materials, water, and equipment for testing, and bear all expenses in connection with the testing.  Conduct testing after all equipment is properly installed, electrical services and piping are installed, liquid is flowing, and the pump station is ready for operation.  Correct all defects discovered to the satisfaction of the Contracting Officer, and all tests repeated, at the expense of the Contractor, until the equipment is in proper working order.

-- End of Section --