554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

www.dammonengineering.com

info@dammonengineering.com

State Police Troop L Headquarters

Mandeville, La

HVAC System Replacement

State Project #’s: 01-107-06B-11, F.01003807

Engineer’s Project: 2372

Pre-Design Meeting Minutes

May 21, 2019

3:00 p.m.

Attendees:

David Dammon, Dammon Engineering, Inc

Sgt. Randy Revels, LSP-L

Minutes:

- The following items were discussed during the meeting:

- In order to facilitate the future office build-out in Rm 137 the following were discussed:

  - Relocate one of the return grilles to a location outside the future renovation.  We can increase the return duct size to accommodate the future renovation.

  - Relocate one of the supply grilles to a location to match the corridor of the future renovation.  We can increase the supply duct size to accommodate the future renovation.

- The existing boiler obstructs the double door entry by about 16”; the existing chiller obstructs the same double door, but on the other side of the doors, by about 6”.  The unobstructed opening into the mechanical room is approximately 49.5”

- All restrooms and showers currently have both supply and exhaust grilles.  Update the plans to reflect this information.