Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99 (R 09/01)

MASTERSPEC Short Form Copyright 1999 (R 09/01), The American Institute of Architects (AIA)

SECTION 15181 - HYDRONIC PIPING
PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes piping, special-duty valves, and hydronic specialties for hot-water heating, chilled-water cooling, and condenser water systems; makeup water for these systems; blowdown drain lines; and condensate drain piping.

B. See Division 15 Section "Basic Mechanical Materials and Methods" for general piping materials and installation requirements.

C. See Division 15 Section "Hydronic Pumps" for pumps, motors, and accessories for hydronic piping.

D. See Division 15 Section "HVAC Instrumentation and Controls" for temperature-control valves and sensors.

1.2 SUBMITTALS

A. Product Data:  For each type of special-duty valve indicated.  Include flow and pressure drop curves based on manufacturer's testing for diverting fittings, calibrated balancing valves, and automatic flow-control valves.

B. Shop Drawings:  Detail fabrication of pipe anchors, hangers, special pipe support assemblies, alignment guides, expansion joints and loops, and their attachment to the building structure.  Detail location of anchors, alignment guides, and expansion joints and loops.

C. Field quality-control test reports.

Retain first paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

E. Operation and maintenance data.

1.3 QUALITY ASSURANCE

Delete first paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if below is retained.

A. Welding:  Qualify processes and operators according to the ASME Boiler and Pressure Vessel Code: Section IX, "Welding and Brazing Qualifications."

B. ASME Compliance:  Comply with ASME B31.9, "Building Services Piping," for materials, products, and installation.  Safety valves and pressure vessels shall bear the appropriate ASME label.  Fabricate and stamp air separators and expansion tanks to comply with the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

1.4 COORDINATION

A. Coordinate pipe sleeve installations for foundation wall penetrations.

B. Coordinate piping installation with roof curbs, equipment supports, and roof penetrations.  Roof specialties are specified in Division 7 Sections.

C. Coordinate pipe fitting pressure classes with products specified in related Sections.

PART 2 -  PRODUCTS

2.1 PIPES, TUBES, AND FITTINGS

See "Writing Guide" Article in the Evaluations for discussion on this Section's organization and on the most efficient way to edit this Section.

A. General:  Refer to Part 3 "Piping Applications" Article for applications of pipe and fitting materials.

Delete materials not retained in Part 3 "Piping Applications" Article.

B. Copper Tube and Fittings:

1. Drawn-Temper Copper Tubing:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M Type C)].

2. Annealed-Temper Copper Tubing:  ASTM B 88, Type K (ASTM B 88M, Type A).

3. DWV Copper Tubing:  ASTM B 306, Type DWV.

4. Wrought-Copper Fittings:  ASME B16.22.

5. Wrought-Copper Unions:  ASME B16.22.

6. Solder Filler Metals:  ASTM B 32, 95-5 tin antimony.

7. Brazing Filler Metals:  AWS A5.8, Classification BAg-1 (silver).

C. Steel Pipe and Fittings:

1. Steel Pipe, NPS 2 (DN 50) and Smaller:  ASTM A 53, Type S (seamless) or Type F (furnace-butt welded), Grade B, Schedule 40, black steel, plain ends.

2. Steel Pipe, NPS 2-1/2 through NPS 12 (DN 65 through DN 300):  ASTM A 53, Type E (electric-resistance welded), Grade B, Schedule 40, black steel, plain ends.

3. Steel Pipe Nipples:  ASTM A 733, made of ASTM A 53, Schedule 40, black steel; seamless for NPS 2 (DN 50) and smaller and electric-resistance welded for NPS 2-1/2 (DN 65) and larger.

Coordinate flange class with products in other parts of this Section and in related Sections to correlate face size and bolt patterns.

4. Cast-Iron Threaded Fittings:  ASME B16.4; Classes 125 and 250.

5. Malleable-Iron Threaded Fittings:  ASME B16.3, Classes 150 and 300.

6. Malleable-Iron Unions:  ASME B16.39; Classes 150, 250, and 300.

7. Cast-Iron Pipe Flanges and Flanged Fittings:  ASME B16.1, Classes 25, 125, and 250; raised ground face, and bolt holes spot faced.

8. Grooved Mechanical-Joint Fittings:  ASTM A 536, Grade 65-45-12 ductile iron;  ASTM A 47 (ASTM A 47M), Grade 32510 malleable iron; ASTM A 53, Type F, E, or S, Grade B fabricated steel; or ASTM A 106, Grade B steel fittings with grooves or shoulders designed to accept grooved end couplings.

9. Grooved Mechanical-Joint Couplings:  Ductile- or malleable-iron housing and synthetic rubber gasket of central cavity pressure-responsive design; with nuts, bolts, locking pin, locking toggle, or lugs to secure grooved pipe and fittings.

10. Flexible Connectors:  Stainless-steel bellows with woven, flexible, bronze, wire-reinforcing protective jacket; 150-psig (1035-kPa) minimum working pressure and 250 deg F (121 deg C) maximum operating temperature.  Connectors shall have flanged or threaded-end connections to match equipment connected and shall be capable of 3/4-inch (20-mm) misalignment.

11. Packed, Slip, Expansion Joints:  150-psig (1035-kPa) minimum working pressure, steel pipe fitting consisting of telescoping body and slip-pipe sections, packing ring, packing, limit rods, flanged ends, and chrome-plated finish on slip-pipe telescoping section.

12. Gasket Material:  Thickness, material, and type suitable for fluid to be handled; and design temperatures and pressures.

Two paragraphs and associated subparagraphs below may be used for chilled-water, condenser water, and condensate drain lines.  See Evaluations for discussion on product characteristics and maximum temperatures.

D. CPVC Plastic Pipe:  ASTM F 441, Schedules 40 and 80, plain ends.

1. PVC Plastic Pipe Fittings:  Socket-type pipe fittings, ASTM F 438 for Schedule 40 pipe;  ASTM F 439 for Schedule 80 pipe.

2. CPVC Solvent Cement:  ASTM F 493.

E. PVC Plastic Pipe:  ASTM D 1785, Schedules 40 and 80, plain ends.

1. PVC Plastic Pipe Fittings:  Socket-type pipe fittings, ASTM D 2466 for Schedule 40 pipe;  ASTM D 2467 for Schedule 80 pipe.

2. PVC Solvent Cement:  ASTM D 2564.

2.2 VALVES

A. General-Duty Valves:  Gate, globe, check, ball, and butterfly valves are specified in Division 15 Section "[Valves] <Insert Section title>."

B. Calibrated Balancing Valves, NPS 2 (DN 50) and Smaller:  Bronze body, ball type, 125-psig860-kPa working pressure, 250 deg F (121 deg C) maximum operating temperature, and having threaded ends.  Valves shall have calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, and be equipped with a memory stop to retain set position.

C. Calibrated Balancing Valves, NPS 2-1/2 (DN 65) and Larger:  Cast-iron or steel body, ball type, 125-psig860-kPa working pressure, 250 deg F (121 deg C) maximum operating temperature, and having flanged or grooved connections.  Valves shall have calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, and be equipped with a memory stop to retain set position.

D. Pressure-Reducing Valves:  Diaphragm-operated, bronze or brass body with low inlet pressure check valve, inlet strainer removable without system shutdown, and noncorrosive valve seat and stem.  Select valve size, capacity, and operating pressure to suit system.  Valve shall be factory set at operating pressure and have capability for field adjustment.

E. Safety Valves:  Diaphragm-operated, bronze or brass body with brass and rubber, wetted, internal working parts; shall suit system pressure and heat capacity and shall comply with the ASME Boiler and Pressure Vessel Code, Section IV.

F. Plastic Ball Valves:  150-psig (1035-kPa) working pressure, 250 deg F (121 deg C) maximum operating temperature, full port design, 1- or 2-piece body design, CPVC body and ball, polytetrafluoroethylene seats, EPDM seals, and tee handle; with threaded, socket, union, or flanged connections.

G. Plastic Butterfly Valves:  150-psig (1035-kPa) working pressure, 250 deg F (121 deg C) maximum operating temperature, PVC wafer body, polytetrafluoroethylene seats, lever lock handle, and wafer style for installation between flanges.

2.3 HYDRONIC SPECIALTIES

A. Manual Air Vent:  Bronze body and nonferrous internal parts; 150-psig (1035-kPa) working pressure; 225 deg F (107 deg C) operating temperature; manually operated with screwdriver or thumbscrew; with NPS 1/8 (DN 6) discharge connection and NPS 1/2 (DN 15) inlet connection.

B. Automatic Air Vent:  Designed to vent automatically with float principle; bronze body and nonferrous internal parts; 150-psig (1035-kPa) working pressure; 240 deg F (116 deg C) operating temperature; with NPS 1/4 (DN 8) discharge connection and NPS 1/2 (DN 15) inlet connection.

C. Expansion Tanks:  Welded carbon steel, rated for 125-psig (860-kPa) working pressure and 375 deg F (191 deg C) maximum operating temperature, with taps in bottom of tank for tank fitting and taps in end of tank for gage glass.  Tanks shall be factory tested with taps fabricated and labeled according to the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.  Include the following fittings and accessories:

1. Air-Control Tank Fitting:  Cast-iron body, copper-plated tube, brass vent tube plug, and stainless-steel ball check, 100-gal. (379-L) unit only; sized for compression-tank diameter.  Design tank fittings for 125-psig (860-kPa) working pressure and 250 deg F (121 deg C) maximum operating temperature.

2. Tank Drain Fitting:  Brass body, nonferrous internal parts; 125-psig (860-kPa) working pressure and 240 deg F (116 deg C) maximum operating temperature; designed to admit air to compression tank, drain water, and close off system.

3. Gage Glass:  Full height with dual manual shutoff valves, 3/4-inch- (20-mm-) diameter gage glass, and slotted-metal glass guard.

D. In-Line Air Separators:  One-piece cast iron with an integral weir designed to decelerate system flow to maximize air separation at a working pressure up to 175 psig (1206 kPa) and liquid temperature up to 300 deg F (149 deg C).

E. Air Purgers:  Cast-iron body with internal baffles that slow the water velocity to separate the air from solution and divert it to the vent for quick removal.  Maximum working pressure of 150 psig (1035 kPa) and temperature of 250 deg F (121 deg C).

F. Bypass Chemical Feeder:  Welded steel construction; 125-psig (860-kPa) working pressure; 5-gal. (19-L) capacity; with fill funnel and inlet, outlet, and drain valves.

1. Chemicals:  Specially formulated, based on analysis of makeup water, to prevent accumulation of scale and corrosion in piping and connected equipment.

G. Diverting Fittings:  125-psig (860-kPa) working pressure; 250 deg F (121 deg C) maximum operating temperature; cast-iron body with threaded ends, or wrought copper with soldered ends.  Indicate flow direction on fitting.

H. Y-Pattern Strainers:  125-psig (860-kPa) working pressure; cast-iron body (ASTM A 126, Class B), flanged ends for NPS 2-1/2 (DN 65) and larger, threaded connections for NPS 2 (DN 50) and smaller, bolted cover, perforated stainless-steel basket, and bottom drain connection.

I. Flexible Connectors:  Stainless-steel bellows with woven, flexible, bronze, wire-reinforcing protective jacket; 150-psig (1035-kPa) minimum working pressure and 250 deg F (121 deg C) maximum operating temperature.  Connectors shall have flanged- or threaded-end connections to match equipment connected and shall be capable of 3/4-inch (20-mm) misalignment.

J. Packed, Slip, Expansion Joints:  150-psig (1035-kPa) minimum working pressure, steel pipe fitting consisting of telescoping body and slip-pipe sections, packing ring, packing, limit rods, flanged ends, and chrome-plated finish on slip-pipe telescoping section.

PART 3 -  EXECUTION

3.1 PIPING APPLICATIONS

Coordinate applications below with materials specified in this Section.  Pipe sizes at which joining methods change are between NPS 2 and NPS 2-1/2 (DN 50 and DN 65).  Adjust this change point to suit personal preference.  Soldered joints for pipes larger than NPS 2 (DN 50) may not meet system pressures.

A. Hot and Chilled Water:  Aboveground, use Type L (Type B) drawn-temper copper tubing with soldered joints or Schedule  [40] [30] [20] steel pipe with threaded joints.  Belowground or within slabs, use Type K (Type A) annealed-temper copper tubing with soldered joints.  Use the fewest possible joints belowground and within floor slabs.

B. Condenser Water:  Aboveground, use Type L (Type B) drawn-temper copper tubing with soldered joints or Schedule  [40] [30] [20] steel pipe with threaded joints.  Belowground or within slabs, use Type K (Type A) annealed-temper copper tubing with brazed joints.

Select paragraph above or first paragraph below.

C. Condenser Water:  Schedule  [40] [80], [PVC] [CPVC] pipe with solvent-welded joints.

D. Condensate Drain Lines:  Type L (Type B) drawn-temper copper tubing with soldered joints or Schedule 40, PVC pipe with solvent-welded joints.

3.2 VALVE APPLICATIONS

A. Unless otherwise indicated, use the following general-duty valve types for applications indicated:

1. Shutoff Duty:  Gate, ball, and butterfly valves.

2. Throttling Duty:  Globe, ball, and butterfly valves.

3. Install shutoff duty valves at each branch connection to supply mains, at supply connection to each piece of equipment, unless only one piece of equipment is connected in the branch line.  Install throttling duty valves at each branch connection to return mains, at return connections to each piece of equipment, and elsewhere as indicated.

4. Install check valves at each pump discharge and elsewhere as required to control flow direction.

B. Unless otherwise indicated, use the following special-duty valve types for applications indicated:

1. Install calibrated balancing valves in the return water line of each heating or cooling element and elsewhere as required to facilitate system balancing.

2. Install safety valves on hot-water generators and elsewhere as required by the ASME Boiler and Pressure Vessel Code.  Install safety-valve discharge piping, without valves, to floor.  Comply with the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1, for installation requirements.

3. Install pressure-reducing valves on hot-water generators and elsewhere as required to regulate system pressure.

3.3 PIPING INSTALLATIONS

A. Install drains, consisting of a tee fitting, NPS 3/4 (DN 20) ball valve, and short NPS 3/4 (DN 20) threaded nipple with cap, at low points in piping system mains and elsewhere as required for system drainage.

B. Install piping at a uniform grade of 0.2 percent upward in direction of flow.

C. Reduce pipe sizes using eccentric reducer fitting installed with level side up.

D. Unless otherwise indicated, install branch connections to mains using tee fittings in main pipe, with the takeoff coming out the bottom of the main pipe.  For up-feed risers, install the takeoff coming out the top of the main pipe.

E. Install strainers on supply side of each control valve, pressure-reducing valve, solenoid valve, in-line pump, and elsewhere as indicated.  Install NPS 3/4 (DN 20) nipple and ball valve in blowdown connection of strainers NPS 2 (DN 50) and larger.  Match size of strainer blowoff connection for strainers smaller than NPS 2 (DN 50).

F. Anchor piping for proper direction of expansion and contraction.

3.4 HANGERS AND SUPPORTS

Piping support must account for expansion and contraction, vibration, and dead load of piping and its contents, and seismic bracing requirements.

A. Hanger, support, and anchor devices are specified in Division 15 Section "[Hangers and Supports] <Insert Section title>."  Comply with requirements below for maximum spacing of supports.  Install the following pipe attachments:

1. Adjustable steel clevis hangers for individual horizontal piping less than 20 feet (6 m) long.

2. Adjustable roller hangers and spring hangers for individual horizontal piping 20 feet (6 m) or longer.

3. Pipe Roller:  MSS SP-58, Type 44 for multiple horizontal piping 20 feet (6 m) or longer, supported on a trapeze.

4. Spring hangers to support vertical runs.

5. On plastic pipe, install pads or cushions on bearing surfaces to prevent hanger from scratching pipe.

Verify actual supported loads for hanger sizes and spacing.  Consult structural engineer.  Spacing and sizes below are from the 1996 ASHRAE HANDBOOK--"HVAC Systems and Equipment."

6. Install hangers for steel piping with the following maximum spacing and minimum rod sizes:

a. NPS 3/4 (DN 20):  Maximum span, 7 feet (2.1 m); minimum rod size, 1/4 inch (6.4 mm).

b. NPS 1 (DN 25):  Maximum span, 7 feet (2.1 m); minimum rod size, 1/4 inch (6.4 mm).

c. NPS 1-1/2 (DN 40):  Maximum span, 9 feet (2.7 m); minimum rod size, 3/8 inch (10 mm).

d. NPS 2 (DN 50):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (10 mm).

e. NPS 2-1/2 (DN 65):  Maximum span, 11 feet (3.4 m); minimum rod size, 3/8 inch (10 mm).

f. NPS 3 (DN 80):  Maximum span, 12 feet (3.7 m); minimum rod size, 3/8 inch (10 mm).

7. Install hangers for drawn-temper copper piping with the following maximum spacing and minimum rod sizes:

a. NPS 3/4 (DN 20):  Maximum span, 5 feet (1.5 m); minimum rod size, 1/4 inch (6.4 mm).

b. NPS 1 (DN 25):  Maximum span, 6 feet (1.8 m); minimum rod size, 1/4 inch (6.4 mm).

c. NPS 1-1/2 (DN 40):  Maximum span, 8 feet (2.4 m); minimum rod size, 3/8 inch (10 mm).

d. NPS 2 (DN 50):  Maximum span, 8 feet (2.4 m); minimum rod size, 3/8 inch (10 mm).

e. NPS 2-1/2 (DN 65):  Maximum span, 9 feet (2.7 m); minimum rod size, 3/8 inch (10 mm).

f. NPS 3 (DN 80):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (10 mm).

8. Elastic Piping Hanger Spacing:  Space hangers according to pipe manufacturer's written instructions for service conditions.  Avoid point loading.  Space and install hangers with the fewest practical rigid anchor points.

9. Support vertical runs at roof, at each floor, and at 10-foot (3-m) intervals between floors.

3.5 PIPE JOINT CONSTRUCTION

A. Refer to Division 15 Section "[Basic Mechanical Materials and Methods] <Insert Section title>" for joint construction requirements for soldered and brazed joints in copper tubing; threaded, welded, and flanged joints in steel piping; and solvent-welded joints for PVC and CPVC piping.

3.6 HYDRONIC SPECIALTIES INSTALLATION

A. Install manual air vents at high points in piping, at heat-transfer coils, and elsewhere as required for system air venting.

1. Install automatic air vents in mechanical equipment rooms only at high points of system piping, at heat-transfer coils, and elsewhere as required for system air venting.

2. Install dip-tube fittings in boiler outlet.  Install piping to expansion tank with a 2 percent upward slope toward tank.  Connect boiler-outlet piping.

3. Install in-line air separators in pump suction lines.  Install piping to compression tank with a 2 percent upward slope toward tank.  Install drain valve on units NPS 2 (DN 50) and larger.

4. Install combination air separator and strainer in pump suction lines.  Install piping to compression tank with a 2 percent upward slope toward tank.  Install blowdown piping with gate valve; extend to nearest drain.

5. Install bypass chemical feeders in each hydronic system where indicated, in upright position with top of funnel not more than 48 inches (1200 mm) above floor.  Install feeder in bypass line, off main, using globe valves on each side of feeder and in the main between bypass connections.  Pipe drain, with ball valve, to nearest equipment drain.

6. Install expansion tanks above air separator.  Install gage glass and cocks on end of tank.  Install tank fitting in tank bottom and charge tank.  Use manual vent for initial fill to establish proper water level in tank.

a. Support tank from floor or structure above with sufficient strength to carry weight of tank, piping connections, and fittings, plus weight of a full tank of water.  Do not overload building components and structural members.

3.7 TERMINAL EQUIPMENT CONNECTIONS

A. Size for supply and return piping connections shall be same as for equipment connections.

B. Install control valves in accessible locations close to connected equipment.

C. Install bypass piping with globe valve around control valve.  If multiple, parallel control valves are installed, only one bypass is required.

D. Install ports for pressure and temperature gages at coil inlet connections.

3.8 FIELD QUALITY CONTROL

Delete first paragraph below if Contractor will perform testing.

A. Testing Agency:  [Owner will] [Engage] a qualified independent testing and inspecting agency to perform field tests and inspections and to prepare test reports.

B. Prepare hydronic piping and perform testing according to ASME B31.9.  Prepare written report of testing.

3.9 ADJUSTING

A. Mark calibrated nameplates of pump discharge valves after hydronic system balancing has been completed, to permanently indicate final balanced position.

B. Perform these adjustments before operating the system:

1. Open valves to fully open position.  Close coil bypass valves.

2. Check pump for proper direction of rotation.

3. Set automatic fill valves for required system pressure.

4. Check air vents at high points of system and determine if all are installed and operating freely (automatic type), or bleed air completely (manual type).

5. Set temperature controls so all coils are calling for full flow.

6. Check operation of automatic bypass valves.

7. Check and set operating temperatures of boilers, chillers, and cooling towers to design requirements.

8. Lubricate motors and bearings.

3.10 CLEANING

A. Flush hydronic piping systems with clean water.  Remove and clean or replace strainer screens.  After cleaning and flushing hydronic piping systems, but before balancing, remove disposable fine-mesh strainers in pump suction diffusers.

END OF SECTION 15181

HYDRONIC PIPING
15181 - 1

