Copyright 2000 AIA
MASTERSPEC - SHORT FORM
9/00

MASTERSPEC Short Form Copyright 2000, The American Institute of Architects (AIA)

SECTION 15815 - METAL DUCTS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes metal, rectangular ducts and fittings for supply, return, outside, and exhaust air-distribution systems in pressure classes from minus 2- to plus 10-inch wg (minus 500 to plus 2500 Pa).

B. See Division 15 Section "Nonmetal Ducts" for fibrous-glass ducts.

C. See Division 15 Section "HVAC Casings" for factory- and field-fabricated casings for mechanical equipment.

D. See Division 15 Section "Duct Accessories" for dampers, sound-control devices, duct-mounting access doors and panels, turning vanes, and flexible ducts.

1.2 SUBMITTALS

A. Shop Drawings:  Show fabrication and installation details for metal ducts.

1. Penetrations through fire-rated and other partitions.

2. Duct accessories, including access doors and panels.

1.3 QUALITY ASSURANCE

A. NFPA Compliance:

1. NFPA 90A, "Installation of Air Conditioning and Ventilating Systems."

2. NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 SHEET METAL MATERIALS

A. Comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods, unless otherwise indicated.  Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

B. Galvanized Sheet Steel:  Lock-forming quality; complying with ASTM A 653/A 653M and having [G60 (Z180)] [G90 (Z275)] coating designation; ducts shall have mill-phosphatized finish for surfaces exposed to view.

C. Reinforcement Shapes and Plates:  Galvanized-steel reinforcement where installed on galvanized sheet metal ducts.

D. Tie Rods:  Galvanized steel, 1/4-inch (6-mm) minimum diameter for lengths 36 inches (900 mm) or less; 3/8-inch (10-mm) minimum diameter for lengths longer than 36 inches (900 mm).

2.3 SEALANT MATERIALS

A. Joint and Seam Tape:  2 inches (50 mm) wide; glass-fiber-reinforced fabric.

Refer to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for a detailed discussion on seam and joint sealing methods and their applications.  First three paragraphs below describe proprietary systems.  Edit to suit Project.

B. Tape Sealing System:  Woven-fiber tape impregnated with gypsum mineral compound and modified acrylic/silicone activator to react exothermically with tape to form hard, durable, airtight seal.

C. Water-Based Joint and Seam Sealant:  Flexible, adhesive sealant, resistant to UV light when cured, UL 723 listed, and complying with NFPA requirements for Class 1 ducts.

D. Solvent-Based Joint and Seam Sealant:  One-part, nonsag, solvent-release-curing, polymerized butyl sealant formulated with a minimum of 75 percent solids.

E. Flanged Joint Mastic:  One-part, acid-curing, silicone, elastomeric joint sealant complying with ASTM C 920, Type S, Grade NS, Class 25, Use O.

F. Flange Gaskets:  Butyl rubber or EPDM polymer with polyisobutylene plasticizer.

2.4 HANGERS AND SUPPORTS

Verify attachment selection and spacing with structural engineer.

A. Building Attachments:  Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

1. Use powder-actuated concrete fasteners for standard-weight aggregate concretes or for slabs more than 4 inches (100 mm) thick.

2. Exception:  Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 4 inches (100 mm) thick.

B. Hanger Materials:  Galvanized sheet steel or threaded steel rod.

1. Hangers Installed in Corrosive Atmospheres:  Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

2. Strap and Rod Sizes:  Comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for steel sheet width and thickness and for steel rod diameters.

C. Duct Attachments:  Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

D. Trapeze and Riser Supports:  Galvanized-steel shapes and plates complying with ASTM A 36/A 36M.

2.5 RECTANGULAR DUCT FABRICATION

A. Fabricate ducts, elbows, transitions, offsets, branch connections, and other construction according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" and complying with requirements for metal thickness, reinforcing types and intervals, tie-rod applications, and joint types and intervals.

1. Lengths:  Fabricate rectangular ducts in lengths appropriate to reinforcement and rigidity class required for pressure class.

2. Deflection:  Duct systems shall not exceed deflection limits according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

B. Transverse Joints:  Prefabricated slide-on joints and components constructed using manufacturer's guidelines for material thickness, reinforcement size and spacing, and joint reinforcement.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Ductmate Industries, Inc.

b. Nexus Inc.

c. Ward Industries, Inc.

d. <Insert manufacturer's name.>

C. Formed-On Flanges:  Construct according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," Figure 1-4, using corner, bolt, cleat, and gasket details.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Ductmate Industries, Inc.

b. Lockformer.

c. <Insert manufacturer's name.>

2. Duct Size:  Maximum 30 inches (750 mm) wide and up to 2-inch wg (500-Pa) pressure class.

3. Longitudinal Seams:  Pittsburgh lock sealed with noncuring polymer sealant.

D. Cross Breaking or Cross Beading:  Cross break or cross bead duct sides 19 inches (480 mm) and larger and 0.0359 inch (0.9 mm) thick or less, with more than 10 sq. ft. (0.93 sq. m) of nonbraced panel area unless ducts are lined.

PART 3 -  EXECUTION

3.1 DUCT APPLICATIONS

A. Static-Pressure Classes:  Unless otherwise indicated, construct ducts according to the following:

Revise pressure classes in subparagraphs below to suit Project, or delete if pressure classes are indicated on Drawings.  If not indicated, contractors will assume a default pressure class of 1-inch wg (250 Pa) according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

1. Supply Ducts:  [1-inch wg (250 Pa)] [2-inch wg (500 Pa)] <Insert pressure class>.

2. Supply Ducts (before Air Terminal Units):  [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert pressure class>.

3. Supply Ducts (after Air Terminal Units):  [1-inch wg (250 Pa)] <Insert pressure class>.

4. Supply Ducts (in Mechanical Equipment Rooms):  [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert pressure class>.

5. Return Ducts (Negative Pressure):  [1/2-inch wg (125 Pa)] [1-inch wg (250 Pa)] <Insert pressure class>.

6. Exhaust Ducts (Negative Pressure):  [1-inch wg (250 Pa)] [2-inch wg (500 Pa)] <Insert pressure class>.

3.2 DUCT INSTALLATION

Coordinate duct installation and accessory arrangement with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Construct and install ducts according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," unless otherwise indicated.

B. Install ducts with fewest possible joints.

C. Install fabricated fittings for changes in directions, size, and shape and for connections.

D. Install couplings tight to duct wall surface with a minimum of projections into duct.  Secure couplings with sheet metal screws.  Install screws at intervals of 12 inches (300 mm), with a minimum of 3 screws in each coupling.

E. Install ducts, unless otherwise indicated, vertically and horizontally and parallel and perpendicular to building lines; avoid diagonal runs.

F. Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

G. Install ducts with a clearance of 1 inch (25 mm), plus allowance for insulation thickness.

H. Conceal ducts from view in finished spaces.  Do not encase horizontal runs in solid partitions unless specifically indicated.

I. Coordinate layout with suspended ceiling, fire- and smoke-control dampers, lighting layouts, and similar finished work.

J. Seal all joints and seams.  Apply sealant to male end connectors before insertion, and afterward to cover entire joint and sheet metal screws.

K. Electrical Equipment Spaces:  Route ducts to avoid passing through transformer vaults and electrical equipment spaces and enclosures.

L. Non-Fire-Rated Partition Penetrations:  Where ducts pass through interior partitions and exterior walls and are exposed to view, conceal spaces between construction openings and ducts or duct insulation with sheet metal flanges of same metal thickness as ducts.  Overlap openings on 4 sides by at least 1-1/2 inches (38 mm).

M. Fire-Rated Partition Penetrations:  Where ducts pass through interior partitions and exterior walls, install appropriately rated fire dampers, sleeves, and firestopping sealant.  Fire and smoke dampers are specified in Division 15 Section "Duct Accessories."  Firestopping materials and installation methods are specified in Division 7 Section "Through-Penetration Firestop Systems."

N. Protect duct interiors from the elements and foreign materials until building is enclosed.  [Follow SMACNA's "Duct Cleanliness for New Construction."]

3.3 SEAM AND JOINT SEALING

A. Seal duct seams and joints according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for duct pressure class indicated.

Instruction in subparagraph below exceeds requirements in SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," which does not require sealing of ducts in pressure classes lower than 2-inch wg (500 Pa).  If sealing ducts is required, revise below.

1. For pressure classes lower than 2-inch wg (500 Pa), seal transverse joints.

B. Seal ducts before external insulation is applied.

3.4 HANGING AND SUPPORTING

A. Support horizontal ducts within 24 inches (600 mm) of each elbow and within 48 inches (1200 mm) of each branch intersection.

B. Support vertical ducts at maximum intervals of 16 feet (5 m) and at each floor.

C. Install upper attachments to structures with an allowable load not exceeding one-fourth of failure (proof-test) load.

D. Install concrete inserts before placing concrete.

E. Install powder-actuated concrete fasteners after concrete is placed and completely cured.

1. Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 4 inches (100 mm) thick.

3.5 CONNECTIONS

A. Make connections to equipment with flexible connectors according to Division 15 Section "Duct Accessories."

B. Comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for branch, outlet and inlet, and terminal unit connections.

END OF SECTION 15815

METAL DUCTS
15815 - 1

