FIRE RATED DOOR REQUIREMENTS

PER INTERNATIONAL BUILDING CODE 2003:

MECHANICAL EQUIPMENT ROOMS:   1 HR.

EXIT DOOR TO STAIRS:  1.5 HR.

CORRIDOR DOORS:   20 MIN.

PRESENT STATUS:

EXIT DOORS IN NORTH WALL TO STAIRS ARE 1.5 HR. EXCEPT ON 3RD AND 6TH FLOORS.

DOORS TO CORRIDOR FROM ROOMS 401, 413, AND 503 ARE 20 MIN. RATED WOOD DOORS.

2ND FLOOR DOUBLE DOORS TO ANNEX ARE 3 HR. RATED METAL.

DOUBLE DOORS IN NORTH WALL OF 1ST FLOOR PRESENT MECHANICAL ROOM ARE 1.5 HR. RATED METAL.

2ND FLOOR MECHANICAL ROOM DOOR IS 1 HR. RATED METAL.

3RD FLOOR MECHANICAL ROOM DOOR IS 20 MIN. RATED WOOD.

4TH FLOOR MECHANICAL ROOM DOOR IS 20 MIN. RATED WOOD.

5TH FLOOR MECHANICAL ROOM DOOR IS 20 MIN. RATED WOOD.

6TH FLOOR MECHANICAL ROOM DOOR IS UNRATED WOOD.

