Paul,

My comments are listed below.  Hard copy to follow.

PLANS REVIEW, SOF RIVERINE AND COMBATANT CRAFT OPERATIONS FACILITY

(FY2008 MILCON P-210)

Reference:  (a) CFR 1910.305(j)(7)

Observation (1):  The Boat Storage Building 2442 has slots for 12 boats.

A raised platform is positioned at or above the stern area of stored

boats.  It is unknown if work processes will take place within these

spaces.

Recommendation (1):  If battery maintenance or hazardous material use

will occur within Building 2442, provide emergency eyewash stations.

Depending on the type of battery: reference (a) requires provisions be

made for the diffusion/ventilation of gases from storage batteries.

RESPONSE:

No battery maintenance to be performed in Boat Storage Building 2442. Battery maintenance to be performed in Maintenance Area / Staging Building 2441, which has two emergency eyewash stations and ventilation.

Observation (2):  The Operations Building 2440 and the Boat

Maintenance/Staging Building 2441 are attached to each other. Work

process requiring hazardous material use within the Boat

Maintenance/Staging Building 2441 spaces could result in vapors/fumes

entering the adjacent spaces of Building 2440. Areas of concern include

the Lobby (103), CSS (106), Armory (107) and Vestibule (116).  The plans

specify a 6000 CFM exhaust fan for building 2441.  Details of the

operations of this fan were not available.

Recommendation (2):  To prevent contaminants from entering building

2440, ensure that building 2441 always operates under negative pressure

relative to building 2440.

RESPONSE:

Building 2440 will act in positive pressure relative to Building 2441.

The exhaust fan is thermostatically controlled with a user interface (override) for manual operation if the thermostat does not engage fan operation and ventilation is needed.

Donald Krehely Jr.  CIEC, CMC, CMRS

Supervisory Industrial Hygienist

Naval Hospital Pensacola

Work 850-452-5666 (New Number)

Cell 850-375-0235

Fax   850-452-5260

donald.krehely@med.navy.mil

