	DESIGN COORDINATION AND REVIEW - COMMENTS

NAVAL SPECIAL WARFARE COMMAND, SAN DIEGO, CA
	PROJECT MANAGER:

Terry Artrip, NAVFACSE

	COMMENTS BY:

Sam Martindale, P.E.
	CODE:

 N4412
	PHONE:

619-447-0772
	DATE:

16 Jun. 2009

	PROJECT TITLE AND LOCATION:

MILCON P210, SOF RIVERINE & COMBATANT CRAFT OPS FACILITY (SBT-22) NASA STENNIS SPACE CENTER, MS
	TYPE OF REVIEW:  

100% Design

  

	NO.
	DWG.NO.

or

SPEC.SECT.
	COMMENTS
	A-E RESPONSE

	1
	Dwg C1.2
	Add the sidewalk around the perimeter of the Boat Storage Building. Sidewalk is part of the original proposal and is needed for maintenance access.
	Sidewalk has been added.

	2
	Dwg C3.2
	Detail 26:  Change the tack coat to prime coat applied to the top of the Base Course. A tack coat is be definition applied to an existing asphalt surface.
	Tack coat has been changed to prime coat.

	3
	Dwg C3.3 
	The area between the compound entrance driveway and the pedestrian sidewalk is shown on sheet C4.2 to be finished surface grass.  I think this will be a maintenance problem and we would be better served to simply asphalt pave the surface.
	Concur. We may want to discuss a combination of asphalt / concrete paving.

	4
	Dwg A1.1 
	Please explain the hatch line that falls where the raised Cage Area is labeled. The hatch line is crossing both aisle way and cage area. I don’t see what it is showing.
	The intent is to show a partial section indicating a raised concrete pad for the cages above the walkway.

	5
	Dwg A1.2 
	In the SITUCO room #207, why is the entire north wall flared out between columns?  I see on the furniture plan it is forming a uniform wall for the system furniture.  Does the occupant want the room configured this way?
	This was coordinated between the User and CID, and was deemed desirable.

	6
	Dwg  A1.3
	Section A: the reader should be able to see the raised SEAL Cage service pad, similar to how it shows in section B on sheet A1.4.
	Raised pads will be added to A1.3.

	7
	Dwg A1.4
	You are missing one set of cages and associated raised pad that should show up against the exterior wall on the right side of the page.
	Cage set will be added to A1.4.

	8
	Dwg A1.8
	Seem we could use an exterior ladder and safety cage to allow access to the roof of the Boat Maintenance Building to be able to clean the Clerestory windows.
	RFP only requires exterior window cleaning access for facilities over three stories tall.

	9
	Dwg A2.1
	For convenience and future uses I suggest we keep a standard height exit door at grade level under the platform. I suggest two doors that swing out and located near each of the two center building stairs to the platform.
	Inadequate head clearance available; door not desired by User.

	10
	Dwg A2.4
	Seem we could use an exterior ladder and safety cage to allow access to the roof of the Boat Storage Building to be able to clean the Clerestory windows.
	RFP only requires exterior window cleaning access for facilities over three stories tall.

	11
	Dwg E2.1
	Repeat Comment: Recommend adding a double head fixture (a fixture on opposite side of the pole) to the F11A light pole near the pedestrian walkway between the parking lot and the Riverine Compound
	Concur. We will add the additional fixture to enhance the lighting levels at the pedestrian gate.

	12
	
	
	

	13
	
	
	

	14
	
	
	

	15
	
	
	

	16
	
	
	

	17
	
	
	

	18
	
	
	

	19
	
	
	

	20
	
	
	

	21
	
	
	

	22
	
	
	

	23
	
	
	

	24
	
	
	

	25
	
	
	

	26
	
	
	

	27
	
	
	

	28
	
	
	

	29
	
	
	

	30
	
	
	

	31
	
	
	

	32
	
	
	

	33
	
	
	

	34
	
	
	

	35
	
	
	

	36
	
	
	

	37
	
	
	


