| PROJECT REVIEW COMMENTS |  | Project No. 0LA2083 |  | Agency: USMS Realty PM: Sylvia Cabello |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Location: Kenner, LA |  | Building Name: |  |  |
|  |  | Review Phase: 95% CD Review |  |  | Date: 3/28/12 | Page 1 of 1 |
| Reviewer: Kyle Hantz, P.E. |  |  | Organization: GSA |  |  |  |
| Comm. No. | page No. | COMMENTS ARCH_x_ CIV __ STRC __ MECH ELEC _ _FIRE __ OTHER ___ |  |  | RESOLUTIONS (BY A/E) |  |
| 1 | A203 | Restroom P2 This ceiling needs to be gyp board per the SFO. |  |  |  |  |
| 2 | A204 | Detail A. West door needs 18” on the pull side per ABAAS 404.2.4.1. |  |  |  |  |
| 3 | A501 | How high above the finished floor should window Type “1’ be? |  |  |  |  |
| 4 | A202 | Since room C2 will have vehicles in it, ensure that all doors into this area have door closers so CO will not proliferate into the occupied spaces. |  |  |  |  |