STRUCTURAL INSPECTION
 
Date:
April 14, 2006
Type:
Residential
 RE:
Post-Hurricane Katrina Structural Inspection
Structure:
Wood frame on red brick and concrete piers, vinyl siding, seal tab and terracotta roof 
Owner(s): 
Nick Tedesco



Mailing:
Nick Tedesco
Property: 
919 Lebeau St..




616 E. Lakeshore Dr.


Arabi, La 70032




Carriere, MS 39426


504-913-6933
History:
Mr. Tedesco contacted Dammon Engineering to perform a structural inspection on the above residence.  He was concerned about damage to the structure of the home after hurricane Katrina’s high winds and flood waters.  The home faces the east and there is a drainage ditch behind the residence.  The flood waters reached approximately six feet inside the home.
 
Findings:
After a visual inspection of the home, the following was noted:
 
1. The exterior of the home is intact.
2. Window awnings were damaged by wind. 

3. An inspection of the concrete piers and red brick piers showed no movement of the structure. 

4. The red brick piers showed signs of mortar erosion. 

5. Roof shingles were loosened or missing and the terracotta ridge was blown loose and portions blown off of the home. 

6. The tongue and groove wood floor in the home is buckling. 

7. There are fractures in the cathedral ceiling in the living room. 

8. Ten feet of the tool shed roof is missing. 

  
Sustained winds of 100 mph and gusts to 130 mph from the north were reported by the NOAA and the Louisiana Department of Climatology reported sustained winds of at least 130 mph in the western quadrant of the storm. 
 
Analysis
The damage to the exterior structure of the home is a direct result of high winds, tornadic activities, flood water and flying objects hitting the home.  The mortar of the red brick piers was likely softened by the water and crumbled after the water receded.  The mortar of the red brick piers should be re-pointed.  The tongue and groove wood floors are a direct result of flood waters that remained in the home for days.  It is common that the plywood sub floor is buckled under the wood floor and will need to be replaced.  The fractures in the ceiling were likely caused by movement of the house during the strong winds of the hurricane.  The tool shed roof was likely blown off prior to the flood waters entering the area.
 
Conclusion:
It is my professional opinion that this home is repairable.  After all of the repairs are complete this home will be in good structural condition.  There may be additional damage not seen until the coverings are removed. 
 

Additional Notes:
When work is being accomplished to rebuild the structure, fastenings and nail patterns should meet the new International Code requirements for that work.
 

Information homeowners should know about flood damaged walls and floors, or those damaged by water entry from rain, etc.
The wood stud walls will need to be dried out prior to covering with new wallboard.  In order to dry out the wood studs, one side of the wall will need to be removed and allow sufficient drying time to occur.  Mold remediation should occur as soon as possible.  The American Wood Council states that wood needs to dry out to less than 19% moisture content prior to enclosing wood studs, otherwise the structural integrity could be compromised and mold growth could occur.  Contractors should not re-install wallboard until the moisture content in the stud wall is below 19%.  Houses built using thicker wood products should expect longer dry out times.

 
Sincerely,
 
 
Emmett G. (Pete) Dammon, P.E.
Louisiana License No. 8796
This inspection is limited to the apparent visual conditions of the structural components of this building.  It does not cover, nor attempts to cover, any components, items, and/or conditions which, by their nature or location, are concealed or are difficult or hazardous to inspect, or which require the moving of furniture, flooring materials, rugs, fixtures, appliances, or any component-part nailed, bolted, or screwed down or shut.  No opinions are expressed regarding conditions which could be discovered only by the disassembly of any component parts, special testing, or removal of any concealing objects.

Inspections are made under normal weather conditions, and are not opinions of the conditions of the property and/or structure which may exist under unusual weather conditions, such as, but not limited to floods, heavy rains or snows, high winds, temperature extremes, or any act of God.  Specific hazardous wastes, toxic substances, toxic mold, air and water quality, communicable diseases, asbestos, soil, environmental, radon, carbon monoxide, formaldehyde, building code and termite conditions are not included in this report unless otherwise stipulated.

This report is not a warranty or guarantee of the property inspected, but it is our opinion of its condition at the time inspected.  Our liability shall be limited to reimbursement of the total cost of inspection.


