554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

dammonengineering.com

info@dammonengineering.com

# Structural Inspection

August 17, 2018

For: 	Vanessa Lyles

DC Manager

American Tire Distributors

512 Johnny F. Smith Ave.

Slidell, La. 70460

Construction:

Approximately 50,000.00 Sq. Ft. Warehouse, tilt up concrete wall panels with structural steel roof framing on a conventional foundation.

Scope:

This inspection is limited to a visual inspection of the shell of the building. No Inspection of the mechanical or electrical systems was performed.  This report is as outlined by the National Academy of Building Inspection Engineers and is not an explanation of cause, effect, or engineering.

History:

Dammon Engineering was contacted to request a structural inspection of the referenced bldg due to an on-site inspection dated 07-18-18 that noted cracks in the veneer of the bldg.

Findings:

Upon inspection of the exterior of the building, several items were noted.

The roof of the bldg is sloped to the front, this allows rainwater to sheet flow to the front of the building and into a gutter system and down into down spouts that drain directly onto the concrete paving area and then sheet flows across the concrete loading zone area into a swell located outside the fence on the west side of the property. Two of the downspouts on the northwest side of the bldg drain directly onto a concrete swell which is directed to the concrete paving area of the loading zone but also slope back to the bldg. The rear and sides of the bldg, the rainwater flows down the tilt up walls onto the ground and out to the swells on the sides of the property.

The tilt up concrete walls has several areas that have surface cracks in them around the personal doors/windows and the flat side of the walls. In several areas of the tilt up walls, rust was noted running down the wall due to exposure of the reinforcing in the panels.

It was also noted that the seals in between the tilt up concrete panels are failing and allowing water to enter between the two panels and run down into the foundation. The area between the tilt up walls and the sidewalks/loading zone have lost its seal due to the sealant failing.

The rear and sides of the bldg allow the rainwater to flow to the swells, but the first 8 to 10 inches of the earth next to the bldg have sloped back towards the bldg allowing rainwater under the foundation.

The tilt up walls on the interior of the bldg wasn’t noted to have any cracks in them.

Conclusion:

It is important to note that all foundations settle.  Usually, everything settles together and the fastest rate of settlement occurs in the first year after construction.  By the fifth or sixth year the settlement has exponentially slowed to where there is little danger that something will happen unless caused by weather, expansion & contraction, tree roots, improper drainage, etc.

Recommendation:

The cracks in the tilt up walls do not appear to have compromised the structural integrity of the bldg.  It is my opinion that the structural integrity of this bldg is currently sound, but the foundation will expand and contract with the ground movement and any standing water. See the attached pictures.

It is recommended to have the following items addressed:

- Reseal all the tilt up wall panels.

- Reseal between the sidewalks and concrete paving areas.

- Adjust the concrete swell on the northwest side of the bldg to slope away from the bldg and reseal it.

- Slope the earth away from the bldg on the rear and sides of the bldg.

Sincerely,

Brian Mistich, P.E.