STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana 70806
225-925-4920

HENRY H. FRY
DEPUTY ASSISTANT SECRETARY

AMENDED LETTER

EDWARD GREMILLION, P E, C E
DAMMON ENGINEERING, INC
1095 FLORIDA AVE
SLIDELL, LA  70458-0000	RE:  P0289481
ARC MECHNICAL CONSTRUCTION
BAYOU LIBERTY
SLIDELL, LA  70458-0000

NFPA 101, 2003

BUSINESS
INDUSTRIAL
	
Dear Applicant:

This is to advise that the previous review letter dated 03/16/2005 for this project is hereby amended as follows:

1.	Our review of drawings and/or specifications for the subject project dated3/16/05 is amended as follows:

   a. Revised plans sent by POR appear to comply with the following comments.
 
   b. Revised plans indicate an area of rescue assistance. All requirements for area of rescue assistance included signage and two-way communication are to be provided.

   c. Plans indicate a shower seat. Seat to located on opposite wall to allow for 12" required clear space at seat side of shower. See plan.

   d. Delete reference to item 2h. Revised plans indicate 24" counter height at sink.

   e. Delete reference to item 3. Revised plans indicate required separation.

   f. Delete reference to item 4. Revised plans appear to comply.

   g. Delete reference to items 2d, e f & g. Revised plans appear to comply.

   h. All other items cited in review letter are to remain in effect. 

2.	NOTE: Please enclose a copy of this letter with future submittals or other correspondence pertaining to this project. 

This review applies to the work indicated on the drawings or specifications.

This review shall in no way permit or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

The above amended review is valid if construction starts within 180 days from the above date of the original review letter.

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below, two (2) to three (3) weeks in advance. Approved plans must be available on job site at time of inspection. Certificate of completion must be provided to inspecting Deputy for final inspection.

REVIEWED BY:
LINDA BURCH
PLAN REVIEW DEPUTY

CC:
Arc Mechanical
Slidell Fire Prevention*
City Of Slidell*
New Orleans District*     5045685500
Slidell Fire Prevention*