1. Floor and ceiling tracks Channel shaped, 3-5/8 in. or 5-5/8 in. wide with 1-1/2 in. flanges. Fabricated from No. 18 GSG galv steel. Attached to floor and ceiling with fasteners spaced 24 in. O.C.

2. Steel Studs C-shaped, fabricated from min No. 18 GSG (0.051 in. thick) galv steel, 3-1/2 in. or 5-1/2 in. wide with 1-1/2 in. flanges and 1/2 in. returns (stiffening flanges.) Min yield strength 40,000 psi. See Ill. 12 of Report R7760-1, -2 dated Dec. 11, 1975 or Ill. 15 of Report R7760-3, -4 dated Aug. 23, 1976 for tables containing max allowable axial loads. Report Ills. available from U. S. Steel Corp., Rm. 1846, 600 Grant St., Pittsburgh, PA 15230.

3. Steel Strapping Flat stock, 2 in. wide both sides of insulation, fabricated from No. 18 GSG galv steel. Located horizontally and attached to both sides of the studs at the third points using one No. 6-20 by 1/2 in. self-drilling steel screw at each intersection.

4. Gypsum Board* 1 Hr Rating Two layers of 1/2 in. thick wallboard applied horizontally or vertically. Inner layer attached to studs and tracks with 1 in. long, 0.142 in. diam Type S-12 bugle head screws spaced 12 in. OC beginning 6 in. from the edge. Outer layer attached to the studs and tracks with 1-5/8 in. long, 0.142 in. diam, Type S-12 bugle head screws spaced 12 in. OC beginning 1 in. from the edge. In addition, the outer layer to be attached to the inner layer at the joints with 1-1/2 in. long, 0.210 in. diam Type G bugle head screws spaced 24 in. OC located between studs. 

See Gypsum Board (CKNX) Category for names of manufacturers.

5. Batts and Blankets* 3-1/2 in. thick, 2 ft wide, glass fiber batts. Inserted between each stud to fill the wall cavity. 

CERTAINTEED CORP 

JOHNS MANVILLE INTERNATIONAL INC 

OWENS CORNING

6. Gypsum Sheathing One layer of nominal 1/2 in. thick exterior sheathing, applied vertically and secured to the studs and runner tracks with 1 in. long, 0.142 in. diam, Type S-12 bugle head screws spaced 12 in. OC along the studs and the runner tracks.

7. Exterior Facings 

7b. Steel Siding Horizontal lap type 9 in. wide fabricated (No. 17 GSG) gauge 0.017 in. thick painted aluminum. Interior face of 0.019 in. thick siding lined with 3/8 in. thick unbonded insulation material. Attached to the studs with 1-7/8 in. long, 0.118 in. diam steel screws spaced 9 in. OC along the studs. A starter strip to be fastened to floor runner with 0.118 in. diam screws spaced 12 in. OC.

