STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana  70806
225-925-4920

HENRY H. FRY
DEPUTY ASSISTANT SECRETARY

NEW CONSTRUCTION

EDWARD GREMILLION, P E, C E
DAMMON ENGINEERING, INC
1095 FLORIDA AVE
SLIDELL, LA  70458-0000
RE:  P0326913
ECO OFFICE WAREHOUSE
HWY 190
SLIDELL, LA  70458

NFPA 101, 2003

BUSINESS

Dear Applicant:

This is to advise that we have reviewed the drawings and specifications for the subject proposed construction and have determined that they appear to satisfactorily comply with the adopted laws, codes, rules and regulations of The State Fire Marshal subject to the following requirements:

1.	The scope of this review applies to the new construction of a 4,771 s.f., Shell Only Business Occupancy. 
(Four units @1,193 s.f. each.) 

2.	This review does not apply to work in UNDEVELOPED SPACES indicated in drawings.  Before any work is commenced in that area, plans and specifications shall be reviewed by this office. 

______________________________________________________________________________________

NOTE:  THE FOLLOWING COMMENTS IDENTIFY ISSUES FOR INFORMATIONAL AND CAUTIONARY PURPOSES OR ISSUES THAT COULD NOT BE VERIFIED IN THE SUBMITTED DOCUMENTS.

3.	FOR TENANT BUILDOUT:

Provide complete Electrical design documents including Service Entrance Feeder diagrams, Meter type and location, Transformer Ground fault calculations, panelboard ratings, locations, balanced panel load schedules in amps and KVA, size and ratings of all overcurrent protection devices, GFCI locations, and specify all conductor sizes in accordance with NEC 80.21 (A)(B)(C), 215.5, 215.2 and 220.3 requirements. 

4.	NOTE:  THE FOLLOWING IS A REVIEW FOR COMPLIANCE WITH THE REQUIREMENTS OF THE LOUISIANA STATE UNIFORM CONSTRUCTION CODE IN ACCORDANCE WITH ACT 12 OF THE 2005 FIRST EXTRAORDINARY SESSION OF THE LOUISIANA LEGISLATURE. THIS REVIEW IS PERFORMED AT THE REQUEST OF, AND ON BEHALF OF THE JURISDICTION IN WHICH THIS PROPOSED PROJECT IS LOCATED.
This office will not be responsible for inspections to certify compliance with applicable requirements. Contact the local Building Official or a Louisiana State Uniform Construction Code Council certified third-party provider to arrange for inspections.

Codes Referenced: 	
	2006 International Building Code (IBC) not including Chapters 1, 11, 27, and 29;
	2006 International Existing Building Code (IEBC) not including Chapter 1;
	2006 International Mechanical Code (IMC);
	2000 Louisiana State Plumbing Code (LSPC);
	2006 International Fuel Gas Code (IFGC);
	2005 National Electric Code (NEC) 

5.	Building Planning:
	a) Proposed Occupancy/Use Group Classification:
The occupancy is Group B per IBC Section(s) 304.
	b) Construction Type/Building Limitations:
The construction type is indicated to be Type V-B per IBC Section 602 AND COVER SHEET. 

The proposed construction IS the allowable height and area limitations of Table 503. 

6.	Fire-Resistance-Rated Construction and Interior Finishes:
SHALL BE SPECIFIED IN THE TENANT BUILDOUT. 

7.	Fire Protection Systems:
The building is NOT provided with an automatic sprinkler system. 
The system is NOT required by IBC Section 903.
The building is NOT provided with a fire alarm system. 
The system is NOT required by IBC Section 907. 

8.	Occupants:
	1) Means of Egress:
Refer to Life Safety Code review above for means of egress requirements.

9.	Structural:
SEE COVER SHEET.
NE DEFICIENCIES NOTED. 

10.	Mechanical Systems:
SHALL BE PROVIDED IN THE TENANT BUILDOUT. 

11.	Plumbing Systems:
NO DEFICIENCIES NOTED. 

12.	Fuel Gas:
NO DEFICIENCIES NOTED. 

13.	Electrical Systems: 
SEE LIFE SAFETY CODE COMMENTS. 

Changes to construction in the field which are not consistent with the reviewed documents are not authorized unless reviewed by this office for compliance with Code.  Modifications to reviewed plans must be submitted to this office by the Architect/Civil Engineer for review prior to final inspection.  If an Architect or Civil Engineer is not required by RS 37:155, revisions shall be submitted by the Owner.  Submittals shall include plans, completed application, a minimum $55.00 review fee, and a copy of the most current plan review letter.

Compliance with code requirements for fire protection systems, such as Fire Alarm, Sprinkler and Suppression Systems, is determined by separate shop drawing submittal and is not included in this review.

This review shall in no way permit and/or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

This review is valid for 180 days from the date of this letter.  Construction permits must be issued and/or construction must commence within this time period.

This office requires certification of the completed project in accordance with the approved documents (certificate enclosed).

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below two (2) to three (3) weeks in advance.  The plans stamped reviewed by this office must be available on job site at time of inspection.  Certificate of completion must be provided to the inspecting Deputy for final inspection.

REVIEWED BY:
KENNETH ROBICHAUX
ELECTRICAL ENGINEER

CC:
Eco Builders
St Tammany Fire Protection District No 1*
City Of Slidell*
New Orleans District*     5042194600