554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

dammonengineering.com

info@dammonengineering.com

Lisa de la Fuente, E.I. II

LDH OFFICE OF PUBLIC HEALTH, REGION IX

42354 West Club Deluxe Road, Suite 12

Hammond LOUISIANA 70403

Re: Habaneros Mexican Restaurant Spray Field

5 K-Rain Spray Heads

Madisonville, LA

St. Tammany Parish

Ms. de la Fuente,

In reference to your correspondence of  November 23, 2020 the following information is presented for your consideration.  To specifically address each concern:

- Please provide the name of the certified operator for the wastewater treatment plant and spray irrigation system.

The operator shall be David Curtis of Curtis Environmental (Located in St. Tammany Parish).

2  Please confirm the effluent will not discharge into a receiving stream and will not leave the owner’s property.

The design of the spray field area and its absorption potential is such that all effluent (1995 gallons maximum) will be absorbed into the ground on Habaneros property and thereby none leaving the property.   The calculated daily effluent depth on the spray field area is 0.404 centimeters.  The Abita Silt Loam USDA Soil Infiltration Rate is 1.27 centimeters which is more than adequate to absorb all water (over 300%).  This information was provided in the initial transmittal cover letter and attached information sheets dated September 12, 2020 sent to Mr. Jacob Haffner.   (see USDA Infiltration Rate Sheet and Soil Type Map and Legend)  There is no immediate receiving stream near this property.

3 Please revise the engineering plans to include all design specifications.

Plans sheet SF 101 has been updated to include additional specifications.  (See updated sheet)

4 Please provide a letter from LDEQ confirming no discharge will leave the site.

Please see attached letter of January 5, 2021 from the DEQ signed by Kimberley Corts.

5 Please provide supporting calculations and documentation determining absorption, evaporation, field/land area required, influence of rain and flooding in the area, and the aerosol potential effect on surrounding property.

01-11-2021

Page2

The initial submittal of September 12, 2020 provided supporting calculations and documentation determining absorption field/land area required.  Also see item # 2 in this letter.  The land area is not in a flood zone and can absorb an additionl 0.866 centimeters of water (daily) as rainfall.  Evaporation rates vary with temperature and humidity and are not a major factor in this project.  Transpiration rates and soil absorption handle the bulk of the moisture.

Aerosol potential is low as the spray heads are within 1 foot of ground level limiting elevated spray and formation of aerosols.  The spray heads emit coarse droplets.   The spray area, as previously mentioned in the September 12, 2020 transmittal letter, consists of deciduous trees, hardwoods, grasses and various underbrush’s that also block any potential aerosol migration.  The flora provides a significant transpiration of water.  Spray heads are directed away from the property lines to contain spray within the proposed boundaries.

There is no appreciable effect of aerosols on surrounding properties as the volume of spray water (1995 gallons per day) is a minimal amount.

6  Please revise plans to include a 6 ft, non-climbable fence around the spray irrigation system.

A six foot non-climbable shall be provided at the property boundaries.

The new Habaneros Mexican Restaurant requires this addition to remain in compliance.  The restaurant shall seat 57 patrons (maximum).  At 35 gallons per day (according to LSSC Title 51, Part XIII, Appendix B) the total maximum flow would be 1995 gallons per day.

- The daily maximum effluent flow rate is 2.77 GPM (based on a 12 hour operating basis).

- The spray field will be +/-  20,096 square feet  (40’ Radius per spray head)

- Spray field shall utilize 5 K–Rain spray Heads.

- The Holding Basin shall be 100+ gallons (minimum). (Downstream from the chlorine contact chamber).

- The Holding Basin Retention Time will be +/- 25 minutes at maximum usage.

- There is a 100’ buffer on 2 sides of the property, owned by Habaneros, and adequate room for the proposed spray field.

- There is additional room for supplementary spray field area if necessary.

- There shall be a 10’ buffer on all sides of the spray field.

Additional Documentation:

- LDH Permit P20-09-103-117, April 21, 2020 for Water and Sewerage System

- Modified Plan Sheet Diagram Layout of Restaurant, Spray Field Area and Buffer Area

- Specification Sheet for Irrigation Pump, Item #558223 Model #WE20G05P4-21

- Specification Sheet for Spray Heads, ProPlus Model #11003-CV, Spray Head #2.5

- USDA Infiltration Rate Sheet

- Soil Type Map and Legend

- Letter of January 5, 2021 from the DEQ

01-11-2021

Page 3

The outfall from the Treatment Process shall be routed to a holding basin.  From there the effluent shall be pumped thru a 1-1/2 SDR PVC line to the spray irrigation area.  Spray heads shall be anchored by concrete supports.  After installation, DEQ shall be notified so that the current permit can be modified to a Zero discharge system.

The extended aeration plant is expected to treat wastewater to 15 mg/l BOD and 15 mg/l TSS and 15 mg/l ammonia.  The spray field of 20,096 sqft can adequately disperse the 0.404 cm per day wastewater thru evaporation, transpiration, and absorption.  Due to the minor hydraulic application, no runoff is expected.

In conclusion, this spray field area is more than adequate to successfully mitigate this minor amount of water (equivalent to a kiddie pool of water).

The project is located away from water bodies and streams.  The water is treated and disinfected to LDH and DEQ standards.  This is a straight forward and simple project that benefits the environment while providing economic support for the parish.

Should you have further questions or if more information is required,  please feel free to contact me.

Respectfully,

Brian A. Mistich, P.E.

Dammon Engineering, Inc.

Louisiana and Mississippi

554 Old Spanish Trail

Slidell, Louisiana 70458

985-649-5832 (office)

985-285-4564 (cell)

XC:  Jacob Haffner