## HEAT LOAD
HVAC Calculations | [8 empty] | 1 pane | 2 pane | 3 pane
Project: |  | Location: |  |  |  | North and Shaded |  |  | 30 | 20 | 16
Job#: |  | Date: |  |  |  | NE & NW |  |  | 90 | 70 | 56
[6 empty] | E & W |  |  | 110 | 95 | 85
Windows (per SQ FT) | [5 empty] | SE & SW |  |  | 110 | 100 | 80
|  | Single Pane | Double Pane | Triple Pane | Heat Gain (btuh) | South |  |  | 80 | 70 | 55
North and Shaded |  | 0 | 0 | 0 | 0 | Skylights |  |  | 154 | 147 | 140
NorthEast and NorthWest |  | 0 | 0 | 0 | 0
East and West |  | 0 | 0 | 0 | 0 | Hidden Calcs: |  |  | 1 pane | 2 pane | 3 pane
SouthEast and SouthWest |  | 0 | 138 | 0 | 13800 | North and Shaded |  |  | 0 | 0 | 0
South |  | 0 | 0 | 0 | 0 | NE & NW |  |  | 0 | 0 | 0
Skylights |  | 0 | 0 | 0 | 0 | E & W |  |  | 0 | 0 | 0
[6 empty] | SE & SW |  |  | 0 | 13800 | 0
[6 empty] | South |  |  | 0 | 0 | 0
Walls (per SQFT) | [5 empty] | Skylights |  |  | 0 | 0 | 0
|  |  | SQ FT |  | Heat Gain (btuh)
Masonry above grade (No insulation) |  |  | 0 |  | 0 | Walls |  |  |  |  | btuh/sqft
Masonry above grade (R-5) |  |  | 0 |  | 0 | Masonry above grade (No insulation) |  |  |  |  | 10.9
Masonry above grade (R-11) |  |  | 0 |  | 0 | Masonry above grade (R-5) |  |  |  |  | 3.1
Wood stud wall system (No insulation) |  |  | 0 |  | 0 | Masonry above grade (R-11) |  |  |  |  | 1.6
Wood Stud wall system (R-11 and 1/2"gyp.) |  |  | 0 |  | 0 | Wood stud wall system (No insulation) |  |  |  |  | 7.8
Wood Stud wall system (R-13 and 1/2"gyp.) |  |  | 1715 |  | 3944.5 | Wood Stud wall system (R-11 and 1/2"gyp.) |  |  |  |  | 2.6
Wood Stud wall system (R-19 and 1/2"gyp.) |  |  | 0 |  | 0 | Wood Stud wall system (R-13 and 1/2"gyp.) |  |  |  |  | 2.3
[6 empty] | Wood Stud wall system (R-19 and 1/2"gyp.) |  |  |  |  | 1.7
Ceiling and Roof (per SQFT)
|  |  | SQ FT |  | Heat Gain (btuh)
Ceilings only: | [5 empty] | Roof / Ceiling |  |  |  |  | btuh/sqft
No Insulation |  |  | 0 |  | 0 | Ceiling only |  |  |  | Roof / Ceiling
R-7 |  |  | 0 |  | 0 | No insul | 43 |  |  | No insul | 28
R-11 |  |  | 0 |  | 0 | R-7 | 43 |  |  | R-11 | 28
R-19 |  |  | 2050 |  | 16810 | R-11 | 8.2 |  |  | R-19 | 4.8
R-22 |  |  | 0 |  | 0 | R-19 | 8.2 |  |  | R-22 | 4
R-30 |  |  | 0 |  | 0 | R-22 | 4.8 |  |  | R-26 | 4
R-38 |  |  | 0 |  | 0 | R-30 | 4.8
R-44 |  |  | 0 |  | 0 | R-38 | 2.6
Roof / Ceiling Combo | [5 empty] | R-44 | 2.6
No Insulation |  |  | 0 |  | 0
R-11 |  |  | 0 |  | 0
R-19 |  |  | 0 |  | 0
R-22 |  |  | 0 |  | 0
R-26 |  |  | 0 |  | 0
Floors (per SQFT) | [5 empty] | Floor |  | btuh/sqft
|  |  | SQ FT |  | Heat Gain (btuh) | Over Basement |  | 0
Over Basement |  |  | 0 |  | 0 | Above Grade (R-5) |  | 7.7
Above Grade (R-5) |  |  | 0 |  | 0 | Above Grade (R-11) |  | 1.7
Above Grade (R-11) |  |  | 0 |  | 0 | Below Grade |  | 1.1
Below Grade |  |  | 0 |  | 0
Occupants (per person)
|  |  | # People |  | Heat Gain (btuh)
Occupant Load |  |  | 95.59 |  | 955.9
Lighting
|  |  | SQFT |  | Heat Gain (btuh)
Office Areas |  |  | 0 |  | 0
Retail Areas |  |  | 0 |  | 0
Electric (per kW)
|  |  | kW |  | Heat Gain (btuh)
Building Electrical Load |  |  | 74 |  | 251600
Fresh Air (per CFM)
|  |  | CFM |  | Heat Gain (btuh)
Fresh Air Rate |  |  | 643.765 |  | 19312.95
HVAC Required
Total Required HVAC= | 25.5353 | Tons

## OCCUPANT LOAD
Occupant Load
Function of Space | SQFT | SQFT PER OCC |  | Occupant Count
Accessory Storage Areas, Mechanical Eq. Room | 0 | 300 | gross | 0
Agricultural Building | 0 | 300 | gross | 0
Aircraft hangars | 0 | 500 | gross | 0
Airport Terminal:
Baggage claim | 0 | 20 | gross | 0
Baggage handing | 0 | 300 | gross | 0
Concourse | 0 | 100 | gross | 0
Waiting Areas | 0 | 15 | gross | 0
Assembly:
Gaming Floors (keno,slots,etc.) | 0 | 11 | gross | 0
Assembly with fixed seating |  | Sec. 1004.7
Assembly without fixed seating:
Concentrated (chairs only) | 0 | 7 | net | 0
Standing Space | 0 | 5 | net | 0
Unconcentrated (tables and chairs) | 0 | 15 | net | 0
Bowling Centers (+5 occupants per lane) | 0 | 7 | net | 0
Business Areas | 109 | 100 | gross | 1.09
CourtRooms | 0 | 40 | net | 0
Day Care | 0 | 35 | net | 0
Dormitories | 0 | 50 | gross | 0
Educational:
Classroom Area | 0 | 20 | net | 0
Shops and other vocational rooms | 0 | 50 | net | 0
Exercise rooms | 0 | 50 | gross | 0
H-5 Fabrication and Manufacturing Areas | 0 | 200 | gross | 0
Industrial Areas | 0 | 100 | gross | 0
Insitutional Areas:
Impatient Treatment Areas | 0 | 240 | gross | 0
Outpatient Areas | 0 | 100 | gross | 0
Sleeping Areas | 0 | 120 | gross | 0
Kitchens, Commercial | 900 | 200 | gross | 4.5
Library:
Reading rooms | 0 | 50 | net | 0
Stack Area | 0 | 100 | gross | 0
Locker Rooms | 0 | 50 | gross | 0
Mercantile:
Areas on other floors | 0 | 60 | gross | 0
Basement and grade floor Areas | 0 | 30 | gross | 0
Storage, Stock, and Shipping Areas | 0 | 300 | gross | 0
Parking Garages | 0 | 200 | gross | 0
Residential | 0 | 200 | gross | 0
Skating Rinks, swimming pools:
Rink and Pool | 0 | 50 | gross | 0
Decks | 0 | 15 | gross | 0
Stages and Platforms | 0 | 15 | net | 0
Warehouses | 0 | 500 | gross | 0
Per IMC 2009
Dining Areas | 900 | 100 |  | 90
|  |  | ∑= | 95.59

## FRESH AIR
Minimum Ventilation Rates
Occupancy Classification | SQFT |  | OA CFM required | Exhaust CFM req |  | Rp | Pz | Ra | Exhaust rate
Food and Beverage Service: |  |  |  |  | Food and Beverage Service:
Bars, cocktail lounges | 0 |  | 0 |  | Bars, cocktail lounges | 7.5 | 0.18 | 100
Cafeteria, Fast food | 0 |  | 0 |  | Cafeteria, Fast food | 7.5 | 0.18 | 100
Dining Rooms | 900 |  | 634.5 |  | Dining Rooms | 7.5 | 0.18 | 70
Kitchens (cooking) | 0 |  |  | 0 | Kitchens (cooking) |  |  |  | 0.7
Offices: |  |  |  |  | Offices:
Conference Rooms | 0 |  | 0 |  | Conference Rooms | 5 | 0.06 | 50
Office Spaces | 109 |  | 9.265 |  | Office Spaces | 5 | 0.06 | 5
Reception Areas | 0 |  | 0 |  | Reception Areas | 5 | 0.06 | 30
Telephone / data entry | 0 |  | 0 |  | Telephone / data entry | 5 | 0.06 | 60
Main Entry Lobbies | 0 |  | 0 |  | Main Entry Lobbies | 5 | 0.06 | 10
Public Spaces: |  |  |  |  | Public Spaces:
Corridors | 0 |  | 0 |  | Corridors |  | 0.06
Toilet Rooms (fixtures) | 3 |  |  | 210 | Toilet Rooms |  |  |  | 70
Storage: |  |  |  |  | Storage:
Warehouses | 0 |  | 0 |  | Warehouses |  | 0.06
|  | ∑= | 643.765