STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana  70806
225-925-4920

HENRY H. FRY
DEPUTY ASSISTANT SECRETARY

NEW CONSTRUCTION

EMMETT DAMMON
DAMMON ENGINEERING
1095 FLORIDA AVE
SLIDELL, LA  70458-0000
RE:  P0287945
QUIZNOS 8336
188 GAUSE BLVD WEST
SLIDELL, LA  70458-0000

NFPA 101, 2003

MERCANTILE CLASS C

Dear Applicant:

This is to advise that we have reviewed the drawings and specifications for the subject proposed construction and have determined that they appear to satisfactorily comply with the adopted laws, codes, rules and regulations of The State Fire Marshal subject to the following requirements:

1.	This project is reviewed in accordance with the requirements of the 2003 Edition of the NFPA 101 Life Safety Code.  Effective January 1, 2004, the 2000 Edition of the International Building Code (IBC) was adopted as part of the Louisiana State Uniform Construction Code.  This project is subject to the requirements of that code.  The Office of the State Fire Marshal does not review for compliance with the IBC requirements except as noted in RS 40:1728 and LAC 55:V:305. 

Changes to construction in the field which are not consistent with the reviewed documents are not authorized unless reviewed by this office for compliance with Code.  Modifications to reviewed plans must be submitted to this office by the Architect/Civil Engineer for review prior to final inspection.  If an Architect or Civil Engineer is not required by RS 37:155, revisions shall be submitted by the Owner.  Submittals shall include plans, completed application, a minimum $55.00 review fee, and a copy of the most current plan review letter.

Compliance with code requirements for fire protection systems, such as Fire Alarm, Sprinkler and Suppression Systems, is determined by separate shop drawing submittal and is not included in this review.

This review shall in no way permit and/or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

This review is valid for 180 days from the date of this letter.  Construction permits must be issued and/or construction must commence within this time period.

This office requires certification of the completed project in accordance with the approved documents (certificate enclosed).

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below two (2) to three (3) weeks in advance.  The plans stamped reviewed by this office must be available on job site at time of inspection.  Certificate of completion must be provided to the inspecting Deputy for final inspection.

REVIEWED BY:
KENNETH ROBICHAUX
ELECTRICAL ENGINEER

CC:
Su Nguyen
Slidell Fire Prevention*
City Of Slidell*
New Orleans District*     5045685500