Date:		02-16-16

To:  		Stephen Campbell

From:		Dammon Engineering

Project:	SMH New Entry Enclosure

Job #:		2253

RE:	Site Investigation

Time/Location: 9:30 am/at site

Attendance:	Stephen Campbell; Chuck Dammon; Jay Morrison

Civil Issues:

- None

Architectural Issues:

- Stephen will provide ceiling tile model number to use in the addition.

Structural Issues:

- Stephen was able to remove the soffit ceiling for inspection above the existing drop off and took many pictures. The existing steel column is wrapped with concrete and where the two pieces come together it is stucco. We could not get a measuring tape on it to verify the size but will measure off the existing dwgs provided.

Mechanical Issues:

- Jay Morrison met us at the site and has determined the existing 5 ton A/C in the lobby will handle the extra square footage of the lobby extension. The new vestibule will be cooled using a ductless mini split. Jay is preparing the cut sheets.

Electrical Issues:

- The existing can lights in the drop off are also connected to the exterior lights and power is from the old section of the building. We have determined that all the power for this addition will come from the new section of the bldg.

Plumbing Issues:

- None identified yet.