January 31, 2002

Mr. Floyd Carwile

Office of State Fire Marshal

Department of Public Safety and Corrections

5150 Florida Blvd.

Baton Rouge, Louisiana 70806

RE:
Camellia Gardens/P0233508

Dear Mr. Carwile,
This letter is to verify the information from the Fire Suppression System Drawings, dated January 2, 2002, submitted to you for approval.

The letter I wrote to you should have stated that in Building #1 & Building #5 the attic would have vertical piping instead of horizontal piping and will be protected by Miracle Vents, as shown in the sketches with the calculations.

These buildings will be submitted at a later date when Coastal Fire Protection has completed the design.  All the riser closets will be heated with electric pump house heaters. (See cut sheet).

We are asking for approval of Building #2, Building #3 & Building #6.

Clarification from your amended letter.

Item #2:

Coastal Fire protection has redrawn the buildings to reflect the exterior stairs.

Item #3:

a. Miracle Vent will only be used in Building #1 & Building #5.

b. Building #2, Building #3 & Building #6 attic sprinkler piping will have insulation over them as shown in the drawings.

Item #4:

I am providing a drawing showing thrust blocks and the general layout of the fire water piping.

Item #5:

Check valve shall be located in the riser room holding water out of the line in the wall.  However, these walls will have insulation.

Item #6:

The hydraulic calculations are being resubmitted with the graph sheet.

Item #7:

I forgot to resubmit the product data in the last submittal.  I am sending them with all the information.

Item #8:

Per NFPA 13-7.2.3.4.2, Exception: Where the area under consideration is a corridor protected by a single row of sprinklers and the openings are not protected, the design area shall include all sprinklers in the corridor to a maximum of seven.  Our calculations included seven sprinklers.

Item #9:

Per NFPA 13R-2.5.2, Exception No.2: lobbies, other than in hotels and motels, foyers, corridors, and halls outside the dwelling unit, with flat smooth ceilings, not exceeding 10 ft. (3.0) in height shall be permitted to be protected with residential sprinklers, with a maximum system demand of four sprinklers.  Our design used this exception.

Thank you,

Chuck Dammon

