January 8, 2003

John Cramer

Plan Examiner

City of Slidell/Permit Dept.

2055 Second Street

Slidell, Louisiana  70458

RE:
New Community Christian Concern Building

Dear John,

The following are answers to your review comments:

1. The pile foundation will be used.  Following final clean up, the area will be brought to original grade prior to driving piles.

2. See Sheet A-1, note at bottom right – factory built roof trusses.  (They will be used.)

3. According to SFPA, Span Tables for other than sleeping rooms.  I usually use the machine grade with 1.6 or 1.7 E, which allows 20’ - 4” in this case.  This corresponds with the CABO visual grading for Southern Pine of E = 1,600,000, for No. 1 nom-dense or No. 2, visual grading.  The CABO allowance is 19’ – 11” for 40lb. live load, at E = 1.6, whereas the Southern Pine Association is based on 30lb. live load.  Please inform me if you see this differently.

4. The rated wall assembly will be to roof.

5. Exit Courts

The exit sidewalk on northside is 5 ft. wide.  The wall and windows will be rated one-hour and have wire glass windows.

6. Agreed – at front handicap ramp, 5 ft. level space will be built in to ramp at 30” below floor.

7. Out building south wall will be rated one-hour.  We propose to do this by installing two layers of 5/8” Gypsum Board on interior wall of out building, assuming it to be the greater risk protecting the larger building that would also have inhabitants.

8. Door leading out of new building from warehouse will be rated ¾ hour.  Windows within 10 ft. of storage building will be wire glass.

Electrical

1. Drawing E-1 shows A/C outlets in attic and outside for A/C #1 & #2.  An outside and inside outlet will be added for A/C #3.  Lights will be installed in attic, near each attic access and A/C unit.

2. Current requirements will be checked when unit is purchased.

3. Kitchen circuits will be on separate circuit breakers from other outlets.

4. Refrigerator circuits will be changed to one circuit, per refrigerator.

5. Is this an Electrical question?  Please clarify.

Mechanical

1. Attic access will be larger than 22 x 36 with all other requirements met.

2. A/C unit moved to side of attic access.

Please feel free to call if you require any further information.

Sincerely,

Emmett G. (Pete) Dammon, P.E.

cc:
Rev. Wellington/Community Christian Concern


Rex Taylor/Contractor

EGD:clh

