September 5, 2001

Mr. William Jensen, Architect

Office of State Fire Marshal

5150 Florida Blvd.

Baton Rouge,  Louisiana  70806

RE:
PO220059/Uniservice Americas, L.L.C.


57174 Hardin Road


Slidell, LA  70458

Dear Mr. Jensen,

Mr. Andrew Franzo of Uniservice Americas asked Dammon Engineering to devise a plan to remove the diesel storage tank from the warehouse in question (PO220059) and design its installation to meet applicable codes in an outdoor location, removing the storage of diesel from the building.

The tank as shown on the drawing will be installed to meet NFPA 30-13, 2-3.2 and 2-3.3, and Table 2-1 Stable Liquids, with less than 2.5 psig operating pressure.  Table 2-1 states that the nearest the tank can be to a property line and/or important building is 5 ft.  We selected a distance of 20 ft. from the building and 30 ft. from the property line.

We ask that you review this submittal for the relocation of the tank only, and delete the requirements of the previous letter.

Sincerely,

Emmett G. (Pete) Dammon, P.E.

EGD:clh

