September 21, 2000

Plan Review

Office of the Fire Marshall

5150 Florida Ave

Baton Rouge, LA  70806

RE;
Woodson School Renovations, Smoke detector


2514 3rd Street


New Orleans, LA  70113-0000


PO # 0201081

ATTN:
Lawrence Delaune


Architect

Dear Sir,

  I spoke to you today on the phone, regarding the smoke detector locations.  You referenced to me 5.5.4.3.1 “Spot type smoke detectors shall be located on the ceiling not less than 4 inches (100mm) from a sidewall to the near edge or, where on a sidewall between 4 inches and 12 inches (100 mm and 300 mm) down from the ceiling to the top of the detector.”

   Dammon Engineering, Inc, plans to have the contractor locate the detectors to meet this code requirement.

   Please indicate your approval of this location.







Sincerely,







Emmett G (Pete) Dammon P.E.

EGD/plc
