STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana  70806
225-925-4920

PAUL SMITH
FIRE MARSHAL

RENOVATION

ROBERT WILTSE
DAMMON ENGINEERING INC
1095 FLORIDA AVE
SLIDELL, LA  70458-0000	
RE:  P0339111
SLIDELL WEST SUITE 151
2170 HWY 190
SLIDELL, LA  70458-0000

NFPA 101, 2006

MERCANTILE CLASS C

Dear Applicant:

This is to advise that we have reviewed the drawings and specifications for the subject proposed construction and have determined that they appear to satisfactorily comply with the adopted laws, codes, rules and regulations of The State Fire Marshal subject to the following requirements:

1.	101:36.1.4  This review is based on an occupancy classification of Mercantile Class C in accordance with 101:6.1.1 and this section, (as indicated on plan review application). 

NOTE:  THE COMMENTS LISTED BELOW IDENTIFY APPARENT DEFICIENCIES DETECTED IN OUR REVIEW OF THE DOCUMENTS SUBMITTED.

2.	101:36.3.2  Separate the Stock Room from other parts of the building by 1-hour fire resistive construction with self-closing 45 minute labeled door/frame assembly or provide automatic sprinkler protection in accordance with Section 9.7 and smoke partitions with self-closing doors in accordance with 8.7.1.2 and 8.4. (Sprinkler piping for isolated hazardous areas connected to domestic water supply shall comply with 101:9.7.1.2). 

______________________________________________________________________________________

NOTE:  THE FOLLOWING COMMENTS IDENTIFY ISSUES FOR INFORMATIONAL AND CAUTIONARY PURPOSES OR ISSUES THAT COULD NOT BE VERIFIED IN THE SUBMITTED DOCUMENTS.

3.	LRS 40:1730.45.A and LAC 55:V:2601  The documentation provided for the subject facility appears to comply with The Commercial Building Energy Conservation Code based on ANSI/ASHRAE/IESNA 90.1- 2004. 

4.	101:8.3.5  Penetrations through rated construction shall be sealed by approved firestop systems or devices tested in accordance with ASTM E-814 or ANSI/UL 1479 or by assemblies of firestopping materials capable of preventing the passage of flames and hot gases when tested and rated in accordance with NFPA 251.
	a)  Notify the District Office identified at the end of this letter for inspection of all completed fire and/or smoke barrier walls before any construction is installed that would conceal such construction and prevent a proper inspection.  Access to randomly selected areas may be required by the inspector at time of final inspection if this notification is not given.
	b)  Provide detailed instructive cut sheets of the fire penetration sealing system used to the inspector at time of inspection.  Random selective sampling by the contractor will be observed by the inspector. 
	
5.	LAC 55:V:303.D  Provide listed portable fire extinguishers in accordance with NFPA 10.
	a)  NFPA 10:1.5.3  Fire extinguishers shall be conspicuously located where they will be readily accessible and immediately available in the event of fire.
	b)  NFPA 10:1.5.6  Fire extinguishers shall not be obstructed or obscured from view.
	c)  NFPA 10:5.1.4  Travel distance to a fire extinguisher shall not exceed 75 feet for Class A, C and D fires. 
	
6.	LRS 40:1731-(Effective 8/15/95)  Provide handicapped accessibility in accordance with ADA-AG (Accessibility Guidelines - September 1994).  This does not include a review for compliance with the Federal Americans with Disabilities (Civil Rights) Act of 1990.  Compliance with state regulations and requirements does not guarantee compliance with federal law.
"CAUTIONARY/INFORMATIONAL" items and paragraph references are noted as follows:
	a)  4.13.9  Door hardware shall comply with this section. Hardware shall not require tight grasping, tight pinching, or twisting of the wrist to operate.
	b)  4.19  Lavatories shall comply with the following:
	1. 4.19.2  Lavatories shall be mounted with a clearance of at least 29" from the floor to the bottom of the apron.  Knee and toe clearances shall comply with Fig. 31.
	2. 4.19.4  Hot water and drain pipes shall be insulated or covered.
	3. 4.19.5 and 4.27.4  Faucets shall not require tight grasping, pinching, or twisting of the wrist to operate.
	4. 4.19.6  Mirrors shall be mounted with the bottom edge not more than 40" from the floor.
	c)  4.22.4 Accessible toilets shall comply with 4.16. 

______________________________________________________________________________________

NOTE:  THE FOLLOWING IS A REVIEW FOR COMPLIANCE WITH THE REQUIREMENTS OF THE LOUISIANA STATE UNIFORM CONSTRUCTION CODE IN ACCORDANCE WITH ACT 12 OF THE 2005 FIRST EXTRAORDINARY SESSION OF THE LOUISIANA LEGISLATURE. THIS REVIEW IS PERFORMED AT THE REQUEST OF, AND ON BEHALF OF THE JURISDICTION IN WHICH THIS PROPOSED PROJECT IS LOCATED.
This office will not be responsible for inspections to certify compliance with applicable requirements. Contact the local Building Official or a Louisiana State Uniform Construction Code Council certified third-party provider to arrange for inspections.

Codes Referenced: 	
	2006 International Building Code (IBC) not including Chapters 1, 11, 27, and 29;
	2006 International Existing Building Code (IEBC) not including Chapter 1;
	2006 International Mechanical Code (IMC);
	2000 Louisiana State Plumbing Code (LSPC);
	2006 International Fuel Gas Code (IFGC);
	2005 National Electric Code (NEC)

7.	Building Planning:
	a)  Proposed Occupancy/Use Group Classification:
The occupancy is Mercantile Group M per IBC Section(s) 309.
	b)  Special Occupancy Areas:
There are no special detailed requirements per IBC Chapter 4.
	c)  Incidental/Accessory Use Areas:
There is an incidental storage use area per IBC Section 508.
	d)  Construction Type/Building Limitations:
The construction type is indicated to be Type IIB per IBC Section 602. 
The proposed construction does not affect the existing height and area of the building. 

8.	Fire-Resistance-Rated Construction and Interior Finishes:
	a)  Separate the Stock Room with minimum 1-hour fire rated construction in accordance with Table 508.2.  Fire barrier shall comply with IBC Section 706. 
	
9.	Fire Protection Systems:
	a)  The existing building is not indicated to be provided with a fire protection system. 
	
10.	Means of Egress:
	a)  Refer to Life Safety Code review above for means of egress requirements. 
	
11.	Structural:
	a)  The scope of work indicated does not appear to affect the existing structure. 
	
12.	Mechanical Systems:
	a)  The termination point of exhaust outlets and ducts discharging to the outdoors shall be located minimum 10 feet from mechanical air intakes, in accordance with IMC Section 501.2.1. THE PROPOSED TOILET EXHAUST LOCATION DOES NOT APPEAR TO COMPLY, see sheet M-1. 
	
13.	Plumbing Systems:
Review for compliance with the requirements of the Louisiana State Plumbing Code [Part XIV (Plumbing) of the State Sanitary Code] is performed at the request of the jurisdiction in which this proposed project is located AND on behalf of the State Health Officer.  In accordance with R.S. 40:4.A(7), R.S. 40:5, and R.S. 40:1730.28.A(5), the State Health Officer and the Office of Public Health of the Department of Health and Hospitals holds the exclusive jurisdiction, control, and authority over Part XIV (Plumbing) of the State Sanitary Code.  Interpretations and/or adjustments to the requirements contained in this code should be directed to that department for ruling.
	a)  Provide at least the minimum type(s) of rest room plumbing fixtures provided for in LSPC Section 407.
THE FOLLOWING NUMBER OF FIXTURES ARE REQUIRED:
	1 MALE WATER CLOSET
	1 FEMALE WATER CLOSETS
	1 MALE LAVATORY
	1 FEMALE LAVATORY
	1 DRINKING FOUNTAIN
Note: In retail stores, a single facility consisting of 1 water closet and one lavatory may be used by both males and females only where the "Usable Building Area" does not exceed 1,500 square feet. The "Usable Building Area" indicated appears to exceed this limitation.
	b)  Provide a floor drain in the toilet room having a removable strainer, the area of which shall not be less than two-thirds the cross sectional area of the trap to which it connects.  Floor drains and traps shall be not less than 2 inches in diameter and the trap shall be equipped with an approved trap primer to maintain the water seal at not less than 2 inches and not more than 4 inches, per LSPC Sections 409.4, 614.4, and 1001. 
	
14.	Electrical Systems: 
	a)  No deficiencies detected. 

Changes to construction in the field which are not consistent with the reviewed documents are not authorized unless reviewed by this office for compliance with Code.  Modifications to reviewed plans must be submitted to this office by the Architect/Civil Engineer for review prior to final inspection.  If an Architect or Civil Engineer is not required by RS 37:155, revisions shall be submitted by the Owner.  Submittals shall include plans, completed application, a minimum $55.00 review fee, and a copy of the most current plan review letter.

Compliance with code requirements for fire protection systems, such as Fire Alarm, Sprinkler and Suppression Systems, is determined by separate shop drawing submittal and is not included in this review.

This review applies to work indicated in the drawings or specifications.  Existing portions of the facility of building unaffected by the new work shall comply with LAC 55:103B thru 55:103F.

This review shall in no way permit and/or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

This review is valid for 180 days from the date of this letter.  Construction permits must be issued and/or construction must commence within this time period.

This office requires certification of the completed project in accordance with the approved documents (certificate enclosed).

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below two (2) to three (3) weeks in advance.  The plans stamped reviewed by this office must be available on job site at time of inspection.  Certificate of completion must be provided to the inspecting Deputy for final inspection.

REVIEWED BY:
LAWRENCE DELAUNE
ARCHITECT SUPERVISOR

CC:
Slidell West Partners
Slidell West Partners
St Tammany Fire Protection District No 1*
City Of Slidell*
New Orleans District*     5042194600