March 22, 2005

Mr. Kirk Pichon

Plan Examiner

The City of Slidell

2055 Second Street

Slidell, Louisiana  70458

RE:
3971 Pontchartrain Drive

Dear Mr. Pichon,

Following are answers to your letter dated March 8, 2005, copy attached.

BUILDING

1) Please provide drawings from metal building manufacturer, the drawings should include the following information:

1603.1.4 Wind load.

A.  Contractor shall provide at time of submittal.
2) 1603.1.5 Earthquake design data.

A.  Following is the earthquake design analysis for this project.

1. Seismic Group 1

2. Table 16151.1

Site Classification D

3.
Fa = 1.6
Fv = 2.4

4.
SMS = FA (1.6) x S5 (.14) - .224


SM1 = Fv (2.4) x S1 (.06) - .144


SDS = .66 (SM5 - .224) - .147


SD1 = .66 (Sm1 - .144) - .095

From 1616.3 (1), Group 1, = Design Cat. A

From 1616.3 (2) Group 1, Design Cat. C

5. Design Cat. A & C shall follow article 1616.4.1 through 1616.4.4 fro design of structure.

3) 1706.1. Scope.

A.  Contractor shall provide.

1706.1.1 When required.

A. Contractor shall comply. 


1706.1.2 Detailed requirements.

A.  Contractor shall comply with and provide with metal building submittal.
1706.2 Quality assurance plan preparation.

A.  Contractor shall comply with and provide with metal building submittal.
1706.3 Contractor responsibility

A.  Contractor shall comply.
4) 1609.1.4 Protection of openings.

A.  Contractor shall supply wood structural panels per code.
5) 1003.3.1.8 Locks and latches.

A.  Contractor shall comply.
6) Provide documentation on spray applied fire resistive material to be used.

A.  Contractor shall supply.
7) Provide documentation on two hour rated wall assembly (UL design number or other approved testing agency).

A. UL #U419.  Non bearing, four hours
UL #U906
8) Provide wind load calculations and details on 10’ and 11’ high fence.

A.  Please see attached.
9) Provide details on mounting of storefront frames to meet wind loads.

A.  Contractor shall comply. 

10) Provide details on guardrails.

A.  Contractor shall comply.
MECHANICAL

1) Outside air requirements for each individual space shall be based on the use and occupancy of the space.

A. O.K. 

2) 405.1 General.

A.  Contractor shall comply.  

3) An air balance report shall be provided prior to final inspection to verify compliance with Chapter 4.

A. Contractor shall comply. 

4) Table 403.3.

A.  Contractor shall comply.
PLUMBING

1) Need size of main sewer and water lines.

A.  1” water line to restaurant, ¾” water line to all others. 

2) Need location and size of water heaters.

A. Preheat unit in each bathroom/restaurant shall supply needed requirement. 

3) Grease trap and related piping drawing required for A-2 occupancy, if applicable.

A.  Restaurant permit shall supply size and location.
ELECTRICAL

1) 1003.2.11 Means of egress illumination.

A. Electrical contractor shall comply. 

2) 1003.2.11.1 Illumination level.

A.  Contractor shall comply. 

3) 1003.2.11.2 Illumination emergency power.

A.  Electrical contractor shall comply. 

If you have any questions, or require any further information, please feel free to call.
Sincerely,

Emmett G. (Pete) Dammon, P.E.
