[image: image1.jpg]STATE OF LOUISIANA
Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard

Baton Rouge, Louisiana 70806
225-925-4920

H “BUTCH” BROWNING

FIRE MARSHAL
AMENDED LETTER
ROBERT WILTSE RE: P0344526
DAMMON ENGINEERING INC TEXTRON MARINE & LAND
1095 FLORIDA AVE 2585 FRONT ST
SLIDELL, LA 70458-0000 SLIDELT, T.A 70458-0000

NFPA 101, 2006

INDUSTRIAL

Dear Applicant:
This is to advise that the previous review letter dated 04/02/2008 for this project is hereby amended as follows:
1. Disregard item no. 4 of original review letter for this project.

The fire alarm visual notification in the warehouse is not required and the selective locations
indicated in the original document are acceptable as proposed for identifying the location of exit
doors from the large building.

2: NOTE: The rest of the original review letter for this project shall remain applicable. Please enclose a
copy of this letter with future submittals or other correspondence pertaining to this project.

This review applies to the work indicated on the drawings or specifications.

This review shall in no way permit or authorize any omissions or deviations from the specific requirements of the
adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

The above amended review is valid if construction starts within 180 days from the above date of the original review
letter.

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory
inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below, two (2)
to three (3) weeks in advance. Approved plans must be available on job site at time of inspection. Certificate
of completion must be provided to inspecting Deputy for final inspection.

REVIEWED BY:
JAMES WAITE
ARCHITECT

Apr 25, 2008
P0344526 - PAGE 1




