REQUEST FOR PROPOSAL

REPAIRS TO A/C SYSTEM

FOR

SLIDELL CITY COURT

501 BOUSCARAN
SLIDELL, LA  70458
Proposals must be submitted

to

Dammon Engineering, Inc.
1095 Florida Ave.

Slidell, Louisiana  70458

no later than:

JUNE 1, 2006

Call Dammon Engineering, Inc. (649-5832) to arrange for  a site visit, or to ask questions concerning                 the project.  Questions and answers will be related      to all proposers.  Successful proposer will enter           into contract with Slidell City Court.

DAMMON ENGINEERING, INC.
dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS

1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

REQUEST FOR PROPOSALS

SLIDELL CITY COURT

501 BOUSCARAN
SLIDELL, LOUISIANA

JUDGE JAMES LAMZ

Replace Air Conditioning System for Court Room & Lobby
May 17, 2006
The existing A/C system uses three each four ton electric cooling/gas heat units mounted outside the building with supply ducts running in the crawl space below the building and overhead return ducts running in the court room ceiling and down to the units mounted on a pad in the rear of the building.  Hurricane Katrina deposited water above the outside units and their electrical safety switch disconnects.  Water also ruined all of the ductwork below the building and the supply and return ductwork outside the building to approximately six feet above the slab.

Please provide your proposal to furnish all labor, plant, material and equipment to accomplish the following.  All work shall be performed in a workman like manner to provide a complete and operating system.  Work shall be accomplished to meet the latest edition of all governing City, State and National Codes.  Provide start up and six month tune-up services, including all Freon, filters, etc., which are required for proper maintenance and operation.

1. Demolish all existing supply ductwork, A/C units, etc., and all other parts of the system below six feet above the ground, and all exterior return duct.

2. Construct platform per the attached sketch to accommodate the three units.  Platform top elevation shall be three feet above the courthouse floor elevation.  Paint platform with one coat primer and two coats grey Rustoleum.

3. Install three (3) each new four (4) ton (48000 BTU)  cooling, minimum 48,000 BTU heating, each unit.  Units shall be Trane Model YSC048A8EC, minimum seer rating 13.  Electrical Rating: 208 Volt, 3 Phase, 60 HZ.

4. Install new ductwork.

a. New plenums with vibration isolators.

b. Supply duct from unit to registers.  Use same internal size duct as existing or larger.

c. Install new return ducts from building entrance to unit.

d. Use flex duct (exterior grade) below building as replacement.

e. Install new dampers at each register and at duct transitions, as required.

5. Relocate and extend gas piping to heat units.  Install new valves and flex joint for isolation purposes.

6. Relocate electrical feeders to new locations, installing new three pole 250 Volt  rated, NEMA 3R fusible safety switches on the elevated platform, minimum height to be top of platform.  Install new fuses to match load.

7. Replace all supply registers in court room and lobby to match or exceed current design.

8. Replace thermostat.  If A/C units are presently timed for stages, duplicate the existing staging sequence.

9. Provide the services of a certified technician to perform an air balance

10. There are two portable units in the court room, connected to A/C power supply.  Do not turn off until new units are operational.

11. Remove portable units, portable electrical and water connections.  Prepare for pick up by carrier and contact Pete Dammon for instructions.

12. Remove all demolition items from premises.  Leave area clear and clean of all demolition items and scrap from this project.

13. Provide warranties as follows:

a. 1 year on labor

b. 5 years on parts

c. 5 years on compressor

** SEE ATTACHED DIAGRAM**

[image: image1.png]DAMMON ENGINEERING, INC.

dammonengineering.com

P.0O. Box 2830

1095 Florida Avenue
Slidell, Louisiana 70458
Office: (985) 649-5832

Slidell, Louisiana 70459
Fax: {985) 641-5950

L ~ LT o
—_ . 1
e b —
2\ N\ |
Uz
N
\ T
\
\
X N
\
N \— ~ FO0 A f’ "A —
Xi e RiTe”
= “T ATEB ZX3
2 : // \\_I A
{ 4 7 \ i H
~Z 7 _ —
i A—j}l—‘ : SR
Mﬁ"ausw@ﬂ)
L E"m&i*d%;
: T STEBL AKELE

L_\YY/

W2 125017 UH]T's

= Fe Sor U .m/

T

Alc 1N CouRT RooM

Tile REPACE
SLIDELL CATY CovRT
Scale: Date: Engr: DAMMON ENGINEERING
S2.-04 oD ARCRITECTS/ENGINEERS





Dammon Engineering, Inc.
           SLIDELL CITY COURT – A/C WORK
         PAGE 1 OF 4

