UNISTRUT P5500T CHANNELS

MOUNTING DETAILS

Slots in this channel are 1 1/8 “ long and 9/16” wide.  They are designed to accommodate a 5/8” anchor bolt with a washer.

These channels are to be mounted vertically on the face of the building at 5’ on center. 

Cable Tray Bracket #P2946 will be bolted onto the channel using two Channel Nuts #P5510 and two Hex Head Screws # HHC5050150EG that are 1 ½” long.

Pipe Strap product number starts with P2558.  This will be a special order product from UNISTRUT direct. (See list of products to be used for this project for contact information to order.) 

The design calls for a 12” drop starting at the right front corner (when facing the building) to allow rainwater to drain properly. The building is 265’ 1” corner to corner.   

Channels are to be mounted vertically along the face of the building.  

There will be an increase in weight progressively across the building.  The first 8 channels will carry one 10” PVC pipe and the use of an 18” channel is sufficient.

The next 16 channels will carry two 10” PVC pipes and should be 36” in length and be installed using four (4) Wedge Anchors.

The next 24 channels will carry three (3) 10” PVC pipes and should be 48” in length and be installed using five (5) Wedge Anchors.  This includes the extension of the three pipes that wrap around the corner of the building and then turn down 90 degrees.  Three of the 48 “ channels are intended to be used horizontally to support these down drains. 

We recommend the use of “Red Head” Wedge Anchors to install the vertical channel to the side of the building.  This building is concrete so the use of WS5860G 5/8th inch or size 11 metric anchors bolt.  This bolt may be anchored drilling a hole 2 5/8th deep into the concrete.

