International Mechanical Code 2012, Section 510 Hazardous Exhaust System.

Ducts used to convey hazardous exhaust shall be constructed of approved G90 galvanized sheet steel, with a minimum nominal thickness as specified in Table 510.8. 12” Round duct shall be a minimum nominal thickness of 0.034” (22 gauge).

Duct joints shall be made tight with lap joints having a minimum lap of 1 inch (25 mm). Joints used in NSI/SMACNA Round Industrial Duct Construction Standards and ANSIISMACNA Rectangular Industrial Duct Construction Standards are also acceptable.

Ducts shall have a clearance to combustibles of 1 inch.

The exhaust duct shall terminate not less than 10 feet from any fresh air intakes.

The duct system shall connect to the existing exhaust fan utilizing a flange and immediately turn 90° upwards.  It shall then turn 90° back over the Paint Kitchen and extend past the exhaust coming from the paint booth.  Turn 90° toward the exterior wall and penetrate the exterior wall.  On the exterior the duct shall turn 90° upwards and extend to an elevation above the roof line.  Terminate the duct with a weatherproof cap.