# IBC Building Code Analysis

Date							Dammon Engineering Project Number

August 27, 2013					-

Dammon Engineering Project Name and Address

Chamber of Commerce Building

# Site Data

# Site Address

Front St., Slidell, LA

# Building Code Search

# Applicable Code

# IBC 2009

Occupancy type of Group(s) (IBC 2009 Chapter 3)

Business

Construction Type(s) (Table 503)

VA	8,170 S.F.

# Allowable Height and Building Area

# Limited by Type of Construction

Maximum Height in Stories (Section 503 & 504, table 503)

2

Maximum Area in Square Feet (Section 503, 506 & 507, table 503)

9,000 S.F.

# Mixed Use and Occupancy

# Section 508

Incidental Accessory Occupancies (HR) (Table 508.2.5)

Room or area						Separation

# N/A

Required Separation or Occupancies (HR) (table 508.4)

N/A

# Fire resistance Rating Requirements for Building Elements

# Chapter 6, table 601

# Structural Frames

0

# Exterior Bearing Walls

0

# Interior Bearing Walls

0

# Exterior Non-bearing Walls

0

# Interior Non-bearing Walls

0

Floor Construction (including supporting beams and joists)

# 0

Roof Construction (including supporting beams and joists)

# 0

Fire Resistance rating for exterior walls based on fire separation distance (table 602)

0

# Maximum Area of Exterior Wall Openings

# Table 705.8

# Notes on specific, pertinent plan issues

15’ Separation unlimited	(unprotected, sprinklered)

# Fire Walls

# Section 706, table 706.4

Required?

No

If YES then note required rating

# N/A

# Fire Barriers

# Section 707

Shaft Enclosure(s) – Note required rating (Section 708.4)

No – per 708.2.7.1

Exit Enclosure – Note required rating (Section 1022.1)

# 1 hour

Exit Passageway – Note required rating (Section 1023.3)

# 1 hour

Horizontal Exit – Note required rating (section 1025.2)

# 2 hours

Atriums – Note required rating (Section 404.6)

# N/A

Separation from Stage (Section 410.5)

# N/A

# Occupant Loads

(IBC 2009. Section 1004, Table 1004.1.1)

# First Floor

Occupancy/Function of space		Floor area per occupant (SF)	x actual SF	Occupant Load

B					100 s.f.	per occupant		4,085 s.f.	41

# Total Occupant Load – First Floor

41

# Second Floor

Occupancy/Function of space		Floor area per occupant (SF)	x actual SF	Occupant Load

B					100 s.f.	per occupant		4,085 s.f.	41

# Total Occupant Load – Second Floor

41

# Exit Requirements

(IBC 2009. Section 1005)

# Number of accessible means of egress required per floor (Table 1015.1 & 1021.1)

Floor							# Means of Egress Required

First Floor						2

Second Floor						1	Per 101:38.2.4.6

# Total width of exits

(Occupant load/# of Means of Egress) x (Factor in Section 1005)

Occupant Load		# of exits provided		Multiplier (Section 1005.1)	Minimum Exit Width

82			4				0.2				16.4”

Maximum Exit Access Travel Distance (Table 1016.1)

100’

Minimum Corridor Width (Section 1018.1 & Section 1005.1)

# 44”

Maximum Dead End Corridor (1018.4)

# 20’

Maximum Common Path of Travel (1014.3)

100’

# Corridors

Corridor Fire-Resistance Rating (Table 1018.1)

B – 0 hours

# Stair Requirements

(IBC 2009. Section 1009)

# Stairway Width (Table 1015.1 & 1021.1)

# Total width of Exits

(Occupant Load/# of Means of Egress) X (Factors in Section 1005) or 44” (whichever is greater)

Occupant Load		# of Stairways		Multiplier (Section 1005)		Minimum Stairway Width

41			1			0.2 = 8.2”				44” per Table 1018.2

# NFPA 101 Life Safety Code Analysis

# Building  Code Search

Applicable Code(s)

# NFPA 101 Life Safety Code 2009

Occupancy Type(s) and Chapter(s)

Business (Chapter 39)

Multiple, mixed, or separated occupancy (reference:  Chapter 6)

N/A

Required separation of occupancies (reference:  Chapter 6, Table 6.1.14.4.1)

# N/A

Classification of hazard of contents (reference:  Occupancy Chapter and 6.2.2; specify low, ordinary, or high)

# Ordinary

Construction Type(s) (reference:  Chapter 8, Table A.8.2.1.2 and Commentary Table 8.1 in Handbook)

# V (000)

Minimum Construction Requirements (reference:  Occupancy Chapter)

# Sprinklered

Applicable Definitions (reference:  Chapter 3)

xxx

# Occupancy

# Occupant Load Calculations (reference:  Table 7.3.1.2)

# First Floor

Occupancy/Function of space		Floor area per occupant (SF)	X actual SF	Occupant Load

Business				100 s.f.				4,085 s.f.	41

# Total Occupant Load – First Floor

41

# Second Floor

Occupancy/Function of space		Floor area per occupant (SF)	X actual SF	Occupant Load

Business				100 s.f.				4,085 s.f.	41

# Total Occupant Load – Second Floor

82

# Incidental Use Areas and Required Separation

Room or area						Separation

# N/A

# Means of Egress

Number of Exits (reference:  Occupancy Chapter and Chapter 7)

# 2

Minimum Exit Separation Distance for Remotely Located Exists (reference:  Section 7.5; specify ½ or 1/3 diagonal distance of area served)

1/3 diagonal	33’-0”

Maximum Dead-end Corridors (reference:  Occupancy Chapter and Table A.7.6)

# 50’

Maximum Common Path of Travel Distance (reference:  Occupancy Chapter and Table A.7.6)

# 75’

Maximum Travel Distance to Exists (reference:  Occupancy Chapter and Table A.7.6)

# 100’

Area of Refuge Requirements (reference:  Occupancy Chapter and 7.2.12)

# N/A

Corridor or Passageway Width Requirements (Reference:  Occupancy Chapter, Table 7.2.2.2.1.1(a) or (b), and Table 7.2.2.2.1.2(B))

xxx

Stair Width Requirements (reference:  Occupancy Chapter, Table 7.2.2.2.1.1(a) or (b), and Table 7.2.2.2.1.2(B))

# 44”

Accessibility Requirements for Egress Components (7.5.4)

xxx

Capacity of Means of Egress (Reference:  7.3 and Table 7.3.3.1)

Component		Occupant Load		x Capacity Factor		Minimum Width

Exits			41			0.2				8.2”

# Main entrance must be sized to accommodate ½ occupant load of building.

# Fire Resistance Rating Requirements

# Chapter 8

Exterior Bearing Walls (reference Table A.8.2.1.2 based on construction type)

# 0

Interior Bearing Walls (reference Table A.8.2.1.2 based on construction type)

# 0

Columns (reference Table A.8.2.1.2 based on construction type)

# 0

Beams, Girders, Trusses, and Arches (Reference Table A.8.2.1.2 based on construction type)

# 0

Floor – Ceiling Assemblies (Reference Table A.8.2.1.2 based on construction type)

# 0

Roof – Ceiling Assemblies (reference Table A.8.2.1.2 based on construction type)

xxx

Interior Non-bearing Walls (reference Table A.8.2.1.2 based on construction type)

# 0

Exterior Non-bearing Walls (reference Table A.8.2.1.2 based on construction type)

# 0

Shaft Enclosure (Section 8.6.5)

# 0 hour

Exit Enclosure

xxx

# Exit Passageway / Exit Access Corridors

xxx

# Horizontal Exit

2 hour

Atriums

# N/A

# Mezzanines

N/A

# Concealed Spaces and Draftstops

xxx

Storage, Boiler, or Furnace Rooms

# N/A

Communicating Spaces (Section 8.6.6)

# N/A

# Opening Protectives

# Chapter 8, Table 8.3.4.2

Component	Walls & Partitions Fire Rating (hr)	Fire Door Assemblies	Fire Window Assemblies (hr)

Elevator:  		1 hr				1 hr

Stairways:  		1 hr				1 hr

Smoke Barriers: 	1 hr				1/3 hr

# Additional Code Requirements

# Occupancy Chapter

# Extinguishment Requirements

Sprinkler (required)

Subdivision of Building Space

N/A

# Detection, Alarm, and Communications Systems

No

# Emergency Lighting

Per 38.2.6

Special Provisions – Stages and Platforms

N/A

# Other

xxx

# Emergency Lighting

xxx

# Allowable Height and building Area

# Per IBC Equivalent Construction Type (Reference Commentary Table 8.1 in the Handbook)

Construction Type (NFPA)

V (000)

Construction Type (IBC)

VA

Maximum Height in Stories (reference:  IBC Table 503)

3

Maximum Height in Feet (reference:  IBC Table 503)

55 feet

Maximum Area in Square Feet (reference:  IBC Table 503)

18,000 s.f.