Jeremy,

In reference to the request to put steps leading up to the pool (see comment #5):

A newly revised plan indicates that the pool coping top will be elevated 1'- 2.75" above the deck (14.75").  The Architect and owner have indicated they do not want steps.    We feel that this project design no different than a hot tub or spa tub that is elevated and does not require steps nor does this pose a hazard.   This pool is not open to the general public.  We would like to request a variance from placing the step.  (See attached Variance Request)

--------------------------------------------------------------------------------------------------------------------

In reference to the lighting (see comment #15)

The code passage quoted in comment #15 appears to be altered by Region I.  The current code reads :

“Where night swimming is permitted and underwater lighting is used, area pool lighting combined shall be provided at not less than 2 watts per square foot of deck area.”

It does not read:

“Where night swimming is permitted and underwater lighting is [not] used, area pool lighting combined shall be provided at not less than 2 watts per square foot of deck area.”

Lighting shall be provided in the pool in accord with  LAC.51:XXIV.715.A.1 and  LAC.51:XXIV.715.A.2 .        This change shall be indicated on the plans.

------------------------------------------------------------------------------------------------------------------------------

Comments of May 11, 2017 Email

- Comment #5, Please add steps from the deck leading into the pool along the main entrance of the pool.  LAC.51:XXIV.323.D, “Risers for steps for the deck shall be uniform and have a minimum height of 3 3/4 inches and a maximum height of 7 1/2 inches. The minimum tread depth shall be 10 inches.”

- LDH strongly recommends that the barrier on the pool between the pool and the sun deck meet the applicable requirements of the Louisiana State Uniform Construction Code.

- Comment #15, Please provide the watts given for both the underwater pool and deck lighting. LAC.51:XXIV.715.A.1, “Where night activities are permitted and underwater lighting is used, not less than 0.5* watts shall be provided per square foot of pool area. Area lighting shall be provided for the deck areas and directed toward the deck areas away from the pool surface insofar as practical. 0.6 watts per square foot of deck area shall be used.” OR LAC.51:XXIV.715.A.2, “Where night swimming is permitted and underwater lighting is [not] used, area pool lighting combined shall be provided at not less than 2 watts per square foot of deck area.”

--------------------------------------------------------------------------------------------------------------------