May 22, 2002

Ken Shexnayder

Jefferson Parish Dept. of Engineering/Plan Review

1221 Elmwood Park Blvd.

Jefferson, Louisiana  70123

RE:
Proposed Convenience Store/Laundromat


3654 18th Street


Metairie, Louisiana

Dear Ken,

Using the average of 550 gals/day/(washer) water usage for a Laundromat, please accept the following figures for the facility.

1. Average Daily Usage:

a. Washers
       9,900 gal

b. Toilets

            40 gal
Total

9,940 gal/day

2. Maximum Daily Usage:

a. Washers
       11,700 gal

b. Toilets

              50 gal
Total:

11,750 gal/day

Water Meter:

Required maximum 16 gal/minute based on 12-hour day.

Louisiana State Plumbing Code, table 607.9 states that a two inch (2”) pipe and therefore a 2” meter would be more than sufficient, as it will support 77.5 gallons per minute (gpm) at 7.5 ft./sec. flow speed.

Sincerely,

Emmett G. (Pete) Dammon, P.E.

