Chlorine Contact Time

Tank Volume:   120 gallons           90 gallons useful liquid storage

Southern Comfort Lounge :          40 seats  *  25 gallons per seat  =         1000 gallons/day

Tatoo Parlor                         :           2 Employees * 20 gal/day/emp =             40 gallons/day

Used Tire Store                    :           2 Employees * 20 gal/day/emp =             40 gallons/day

Total                                       :                                                                              1080 gallons/day

12 hour operation               =           1.5  gallons usage per minute

1.5 gal/minute  *  30 minutes   =    45 gallons of storage for 30 minute contact time (required)

90 Gallons of storage will exceed the 30 minute contact time required.