## Bruce D. Greenstein

## SECRETARY

### State of Louisiana

###### Department of Health and Hospitals

# Bobby Jindal

## GOVERNOR

PROCEDURES FOR SUBMITTING PLANS AND SPECIFICATIONS

FOR REVIEW AND APPROVAL OF

PUBLIC WATER SYSTEMS, COMMUNITY SEWERAGE SYSTEMS, PUBLIC BUILDINGS, SCHOOLS, INSTITUTIONS, JAILS/PRISONS, PUBLIC SWIMMING POOLS, AND FUNERAL HOMES

The following procedures shall be used when submitting plans and specifications for public water systems, sewerage systems, public buildings, schools, institutions, jails/prisons, swimming pools, and funeral homes for review and approval by the Department of Health and Hospitals (DHH)/Office of Public Health (OPH).  This does not include, however, projects involving the technology of individual home sewage disposal or other sewage systems at or below 3,000 gallons per day (gpd). The plans and specifications for all projects having a design average flow of 3,000 gallons per day or less, or an equivalent organic loading, must be submitted to the local parish health unit.

Following are some common maximum project sizes to be handled by the local parish health units:

3,000	gallons per day design average flow (sewage)

- residential users

- office or factory workers (no food handling or showers)

- trailer sites

- two bedroom apartments

The State Sanitary Code requires that, prior to the start of constructions, approval by DHH be obtained for plans and specifications of the above referenced facilities.  This applies to new facilities as well as any modifications or extensions of existing facilities.  Public water supplies are defined as those which have a minimum of 15 service connections or regularly serve an average of at least 25 persons daily at least 60 days out of the year.

The plans and specifications must be submitted to the Engineering Services Section of the Regional OPH Office in your area. A current map of OPH Regional offices, coverage areas, and engineering services contacts is available on our website at http://www.dhh.louisiana.gov/offices/?id=204.

In order to expedite our handling of your projects, the following suggestions are offered regarding plans and specifications which you submit for approval to the Department of Health and Hospitals:

- A single set of detailed plans and specifications should be submitted at least 60 days prior to the time the approval, comments, or recommendations are desired by the owner.  Plans must be signed, stamped, and dated by a registered professional engineer, licensed to practice in the State of Louisiana.

- A completed design summary package must be submitted.  The applicable design summary pages, which are attached, shall be used.  The design summary package is not a review tool therefore any details relevant to the review should be included in plans and specifications.

- When multiple permits are required for a project (i.e., water and sewer), no permit will be issued until complete plans and specifications meeting all requirements of the state sanitary code for all the permits required for the project have been received.

- Submit a vicinity map showing the project location, the sewage treatment facility location, discharge point, and receiving stream. Include a tracing of the outfall to the first perennial (non–intermittent) waterway in the path of the projected outfall.

- Submit plot plan identifying the lots and including adjacent property usage and ownership.

- Submit layout drawings of the sewage collection and water distribution mains, showing all pump stations, manholes, clean-outs, hydrants, valves, pipe size and materials, sewage main depth, slopes and invert elevations, water main depths, etc., as well as the sewage treatment facility location and the water well location.  Details that do not pertain to the sanitary features need not be included such as storm water drainage and street details.

- Submit detailed drawings of sewage treatment, collection, and pumping facilities and water well, storage and treatment facilities with plan, profile, and end views, depicting dimensions, capacities, materials, and elevations referenced to the North American Vertical Datum of 1988 (NAVD88).

- Where lots are sold, evidence must be submitted showing that the facilities will be maintained in perpetuity.  Ownership by a governmental body is one way to do this.  As a prerequisite to our approval of privately owned facilities, the owner must be set up to own, operate, and maintain the facilities rather than the developing company.  In addition to this agency’s approval, state law requires a profit type utility serving more than ten customers to register with the Louisiana Public Service Commission.

- For extensions to an existing system, information pertaining to the existing system should be submitted.  Please include present population served, design capacity of present system, capacity of lift stations, etc.  The ability of the existing system to absorb the extra loading should be documented.  Also, if the extension is outside the boundaries of a municipality or district, a letter of acceptance from that authority should be included.

- For a sewage treatment plant, a complete description of the effluent outfall pattern shall be submitted.  Depictions, detailed descriptions and definitions of all servitudes or rights-of-way encountered for the entire outfall path shall be provided. Written verification/authorization from the legal entity(ies) associated with said servitudes indicating no objection to the discharge of treated sewer effluent into said servitudes shall be submitted. Written verification/authorization from the local governing body indicating no objection to the proposed point of discharge and outfall path shall be submitted. If the treated effluent will encounter a Louisiana Department of Transportation and Development (LDOTD) right-of-way, a letter of no objection from LDOTD for the discharge of treated sewer effluent into the LDOTD right-of-way shall be provided. It is important that the plant not discharge across privately owned property without benefit of easement before reaching a perennial stream (See Item 3 above).

- Elaborate on whether or not the proposed water well and water treatment facilities and sewage treatment and pumping facilities are located above the 100-year flood plain.   If not, explain the protective measure to be used. Floodplain, Base Flood Elevation/100-Year Flood Elevation, and elevations of the proposed structures shall be shown on the plans.

- The review of the plans and specifications are made, with some exceptions, in accordance with the “Recommended Standards for Wastewater Facilities”, 1990 Edition, and the “Recommended Standards for Water Works”, 2003 Edition, promulgated by the Great Lakes - Upper Mississippi River Board of State and Provincial Public Health and Environmental Managers [available from the Health Education Services – P.O. Box 7126 – Albany, NY  12224 (www.hes.org)].  Design standards for water well construction is contained in the “Louisiana Water Well Rules, Regulations, and Standards”, November, 1985 Edition (LAC 56:I), promulgated by the Louisiana Department of Transportation and Development, Water Resources Division.  Additional Design Standards for water and sewerage facilities are given in Parts XII and XIII, respectively, of the State Sanitary Code.  The state sanitary code is available at http://www.dhh.louisiana.gov/offices/?ID=242 .

- The Louisiana Department of Environmental Quality (DEQ) is responsible for determining the water quality requirements in the State for all wastewater discharges as well as for the issuance of wastewater discharge permits.  State law requires that a discharge permit be obtained from the Department of Environmental Quality, Office of Environmental Services, Water  & Waste Permits Division, P. O. Box 4313, Baton Rouge, LA 70821-4313 (Phone # 225-219-3181) prior to discharge of any wastewater.  You may also be required to obtain a federal permit for the wastewater discharge, about which DEQ can advise you.

- Federal mandate for DEQ to establish Total Maximum Daily Loads (TMDLs) for all water bodies in our state have resulted in lower limits being established for wastewater dischargers to specific receiving streams based on what organic loads the receiving stream may already have and other stream specific data. A copy of your Administrative Completeness Determination letter and Response to Request for Preliminary Determination from DEQ or existing DEQ discharge permit shall be submitted along with this design summary package for all permits involving a wastewater treatment facility. Regarding this you should contact DEQ Water Permits Division, PO Box 4313 Baton Rouge, LA 70821-4313 whose phone number is 225-219-3181.

- If the project involves work or structures in the waters of the State including adjacent wetlands, a permit from the U. S. Army Corps of Engineers may be required.  Examples, of this are water intake structures, pipeline stream crossings, and sewage plant out fall structures.  Regarding this, you should contact the New Orleans District Corps of Engineers, Department of the Army, P. O. Box 60267, New Orleans, LA  70160.  Attention:  LMNOD-SP. Or the Vicksburg District Corps of Engineers, Department of the Army, 4155 Clay Street, Vicksburg, MS 39183-3435. Attention: CEMVK-OD-F

- If the project would have an impact on any surface water body that has been designated as a Scenic River, then a permit may be required from the Louisiana Department of Wildlife and Fisheries.  Regarding this you should contact the Ecological Study Section, Louisiana Department of Wildlife and Fisheries, P. O. Box 14526, Baton Rouge, LA  70898.

- The Operator for Public Water Systems and Community Sewer Treatment and Collection Systems shall hold a current and valid Professional Certification (s) of the required category as set forth in R.S. 40:1141-1151.  Additionally, an Operator shall demonstrate that when not present at the facility, he or she is capable of responding to that location within one (1) hour of being notified that his presence is needed.  For more information regarding Operator Certification, please call the Department of Health and Hospital’s Office of Public Health Operator Certification Unit at (225) 342-7508.

- For water system, wastewater system, and public pool projects only, once the project is complete, the last page titled “CERTIFICATION OF CONSTRUCTION” shall be completed, sealed and signed by the Engineer-of-Record and signed by the contractor then submitted to the office from which the permit was issued. Your permit is not considered final until this step has been completed.

# DESIGN SUMMARY PACKAGE

(Fill Out Applicable Sheets)

| Project: | Southern Comfort Lounge Water Supply |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project Type: |  |  |  |  |  |
| Estimated Project Cost: | $5000.00 |  |  |  |  |
| Engineer: | Brian A. Mistich |  |  |  |  |
| Telephone: | 985-285-4564 |  |  |  |  |
| Parish: | St. Tammany |  | Nearest Town: |  | Slidell |
| Population Served: | 30 |  |  |  |  |
| New System? |  |  |  | Existing System? |  |
| Project to be Owned and Operated By: (include name and address) |  | Mr. Raymond B. Williams 64491 Hwy 434 Lacombe, LA 70445 |  |  |  |
| Proposed Project Will Connect to: (name of water and/or sewer system) |  | Stand Alone |  |  |  |

SEWER COLLECTION SYSTEM

| Project: | n/a |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: |  |  |  |  |  |  |  |  |  |
| General Scope of Project: |  |  |  |  |  |  |  |  |  |
| GRAVITY PIPING | Material (specify ASTM standard and standard dimension ratio-SDR) |  |  |  |  |  |  |  |  |
|  | Size (8 inch minimum diameter) |  |  |  |  |  |  |  |  |
|  | Joints and Materials of Fitting: |  |  |  |  |  |  |  |  |
| ## FORCE MAINS | Material (specify ASTM standard and standard dimension ration-SDR) |  |  |  |  |  |  |  |  |
|  | Size (3 inch minimum diameter without grinder pumps; 1 ¼ minimum diameter with grinder pumps) |  |  |  |  |  |  |  |  |
|  | Joints and Materials of Fitting: |  |  |  |  |  |  |  |  |
| ## LAYOUT | Slope of Gravity Mains |  | %Min. |  |  |  |  | %Max. | %Majority |
|  | Location with Respect to Water Lines: |  |  | Maintain 18” Minimum Vertical Clearance @ Crossings? |  |  |  |  | Yes No |
|  |  |  |  | Maintain 6’ Minimum Horizontal Clearance? |  |  |  |  | Yes No |
|  | Maximum Distance Between Manholes: |  |  |  |  |  |  |  |  |
|  | Number of Surface Water Crossings/Encounters: |  |  |  |  |  |  |  |  |
|  | Other Comments: (Manhole Construction, Highway Crossing, etc.) |  |  |  |  |  |  |  |  |
| Deflection Testing? Yes No |  |  |  |  |  |  | Hydrostatic Testing? Yes No |  |  |
| NAME OF CERTIFIED OPERATOR: |  |  |  |  |  |  |  |  |  |

WATER WELL

1 of 2

| Project: | Southern Comfort Lounge Water Supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: | Brian A Mistich |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | 7/14/2015 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Site Fenced? Yes No |  |
| General Scope of Project: |  | Water Supply for a Lounge |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Site Location: (also complete the last section of this table) |  | 2209 Gause Blvd East, Slidell, La |  |  |  |  |  |  |  |  |  |  |  |  | 50’ Radius of Ownership? Yes No |  |  |
| Maximum # of Lots (or population): |  |  |  |  |  | 30 persons |  |  |  |  |  |  |  |  |  |  |  |
| INTERNAL STRUCTURE (sketch on separate sheet) |  |  | ## Outer Casing |  |  |  | Linear Feet: |  |  |  |  |  | 340' |  |  |  |  |
|  |  |  |  |  |  |  | Thickness: |  |  |  |  |  | 0.154" |  |  |  |  |
|  |  |  |  |  |  |  | Pounds/Foot: |  |  |  |  |  | 0.72 |  |  |  |  |
|  |  |  |  |  |  |  | Joint: |  |  |  |  |  | unk |  |  |  |  |
|  |  |  |  |  |  |  | Type of Seal to Outer Casing: |  |  |  |  |  | n/a |  |  |  |  |
|  |  |  | ## Inner Casing |  |  |  | Linear Feet: |  |  |  |  |  | n/a |  |  |  |  |
|  |  |  |  |  |  |  | Thickness: |  |  |  |  |  | n/a |  |  |  |  |
|  |  |  |  |  |  |  | Pounds/Foot: |  |  |  |  |  | n/a |  |  |  |  |
|  |  |  |  |  |  |  | Joint: |  |  |  |  |  | n/a |  |  |  |  |
|  |  |  | ## Grouting |  |  |  | Depth of grout: |  |  |  |  |  | 50' |  |  |  |  |
|  |  |  |  |  |  |  | Thickness: |  |  |  |  |  | 1 1/2" |  |  |  |  |
|  |  |  |  |  |  |  | Method With a Setting Time of? |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Screen |  |  |  | Linear Feet: |  |  |  |  |  | 10 |  |  |  |  |
|  |  |  |  |  |  |  | Type: |  |  |  |  |  | slotted pvc |  |  |  |  |
| EXTERNAL STRUCTURE (sketch on separate sheet) |  |  | Casing Head Seal? Yes No |  |  |  |  |  | ## Slab & Motor Foundation? Yes No |  |  |  |  |  |  |  |  |
|  |  |  | ## Well ## Vent |  | Diameter: (½”inch minimum) |  |  |  |  |  | n/a inches |  |  |  |  |  |  |
|  |  |  |  |  | Down-Turned? Terminates 24” above 10-year Flood Level or floor whichever is greater? Twenty Four Mesh Screen? Watertight Seal at Casing? |  |  |  |  |  |  |  |  |  |  |  | Yes No Yes No Yes No Yes No |
|  |  |  | Drawdown Gauge: |  |  |  |  | Type (seal): |  | n/a |  |  |  |  |  |  |  |
|  |  |  | Pump | Type: centrifugal |  |  |  |  |  |  |  |  |  | Power: 120 V |  |  |  |
|  |  |  |  | Capacity (GPM): 10 |  |  |  |  |  |  |  | @ =/- 20 TDH (FT) |  |  |  |  |  |
|  |  |  | Prime Mover: |  | Electric |  |  |  |  |  |  |  |  |  |  |  |  |

WATER WELL

2 of 2

| DISCHARGE PIPING | Discharge Piping Material: pvc |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | ## Down-Turned Smooth-Nozzle Sample Tap? Check Valve? Shutoff Valve? Discharge Bypass? Pressure Gauge? Means of Measuring Flow? |  |  |  | Yes No Yes No Yes No Yes No Yes No Yes No |
| COMPLETION SPECIFICATIONS | ## Disinfection Method: ## (include chlorine dosage and retention time) |  | NSF Sodium Hypochlorite Solution , 3 ppm, 48 minutes contact time |  |  |
|  | Testing to be Performed: residual chlorine |  |  |  |  |
|  | Abandoned Holes? Yes No |  |  |  |  |
| NAME OF CERTIFIED OPERATOR: |  |  |  | Kerry Craig, #44512 |  |
| LOCATIONAL INFORMATION |  | Coordinates: Latitude 30°17’16.0”N Longitude 89°43’53.0”W OR Latitude 00. 00000°N Longitude 00. 00000°W |  |  |  |
|  |  | Geographic Datum: NAD83 WGS84 NAD27 |  |  |  |
|  |  | Collection Method: GPS — DGPS/WAAS enabled? Yes No — Horizontal Accuracy? meters Map Specify: Scale: |  |  |  |

WATER SUPPLY

# BOOSTER STATION

| Project: | n/a |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: |  |  |  |  |  |  |  |  |  |  |  |  |
| Site Location: |  |  |  |  |  |  |  |  |  |  |  |  |
| Water is Transmitted From: |  |  | To: |  |  |  |  |  |  |  |  |  |
| ## CONSTRUCTION |  | ## Exterior Structure | Length: |  | Width: |  |  |  |  |  |  | Height: |
|  |  |  | Floor Material: |  |  |  |  |  |  |  |  |  |
|  |  |  | Material: |  |  |  |  |  |  |  |  |  |
|  |  |  | Ventilation? Yes No |  | Floor Elevation (6” Above Finished Grade?) Yes No |  |  |  |  |  |  |  |
|  |  | ## Interior Structure | Lighting: |  |  |  |  |  |  |  |  |  |
|  |  |  | Heating: |  |  |  |  |  |  |  |  |  |
|  |  |  | Chlorination? Yes No |  |  | ## Type: |  |  |  |  |  |  |
|  |  |  | Floor Slope (3”/10’): |  |  |  |  |  |  |  |  |  |
|  |  | ## Pumping | Number: |  |  |  |  |  |  |  |  |  |
|  |  |  | Type: |  |  |  |  |  |  | Power: |  |  |
|  |  |  | Capacity (GPM): |  |  |  |  |  | @ TDH (FT) |  |  |  |
|  |  | ## Piping | ## Pipes to Pumps |  |  |  | Size: |  |  |  |  |  |
|  |  |  |  |  |  |  | Type: |  |  |  |  |  |
|  |  |  | Pump Discharge Pipe |  |  |  | Size: |  |  |  |  |  |
|  |  |  |  |  |  |  | Type: |  |  |  |  |  |
|  |  |  | Common Discharge Pipe |  |  |  | Size: |  |  |  |  |  |
|  |  |  |  |  |  |  | Type: |  |  |  |  |  |
|  |  |  | Backflow Prevention? Yes No |  |  |  | ## Type: |  |  |  |  |  |
| GENERAL COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |

WATER SUPPLY FINISHED

WATER STORAGE

1 of 2

| Project: |  | Southern Comfort Lounge Water Supply |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: |  | Brian A. Mistich |  |  |  |  |  |  |  |  | Site Fenced? Yes No |
| Date: |  | 7/15/2015 |  |  |  |  |  |  |  |  |  |
| Site Location: |  | 2209 Gause Blvd East, Slidell, La |  |  |  |  |  |  |  |  |  |
| Type of Storage Facility: |  |  |  |  |  |  |  |  |  |  |  |
| Treatment Plant Storage (i.e. clearwell) Elevated Storage Tank |  |  |  |  |  |  |  | Hydropneumatic Pressure Tank Ground Storage Tank |  |  |  |
| ## SIZE | ## Diameter/Depth: |  |  |  |  |  | 18" |  |  |  |  |
|  | Height and/or Length: |  |  |  |  |  | 66" |  |  |  |  |
|  | Elevation: |  |  |  |  |  | 2' above ground level |  |  |  |  |
|  | Shape: |  |  |  |  |  | cylindrical |  |  |  |  |
|  | Capacity (gal): |  |  |  |  |  | 70 |  |  |  |  |
|  | Material (type): |  |  |  |  |  | steel |  |  |  |  |
|  | Wall Thickness: |  |  |  |  |  | unk |  |  |  |  |
|  | Cover Thickness: |  |  |  |  |  | n/a |  |  |  |  |
|  | Floor Thickness: |  |  |  |  |  | n/a |  |  |  |  |
| Base Construction: |  |  |  | steel |  |  |  |  |  |  |  |
| Corrosion Control: |  |  |  | paint |  |  |  |  |  |  |  |
| ## COATING |  | Interior: |  |  |  | unk |  |  |  | Cathodic Protection? Yes No |  |
|  |  | NSF Approved Yes No |  |  |  |  |  |  |  |  |  |
| ## MANHOLE |  | Size: |  |  | n/a |  |  |  |  |  |  |
|  |  | ## Overlap 2”? Water Tight? Accessible? Secure? Yes No Yes No Yes No Yes No |  |  |  |  |  |  |  |  |  |
| OVERFLOW PIPING (n/a for pressure tanks) |  |  | Turned Down 12”-24” Above Grade? Screened? If Flapper, Screened Inside? Splash Pad or Inlet Drainage Structure? Diameter n/a inches |  |  |  |  |  | Yes No Yes No Yes No |  |  |
| VENTS (n/a for pressure tanks) |  |  | Turned Down 24” Above Roof or Sod? Twenty Four Mesh Non-Corrodible Screen? Diameter n/a inches |  |  |  |  |  | Yes No Yes No |  |  |
| GENERAL |  |  | Bypass to Bring Out of Service? Pressure Gauge? Water Level Control Equipment? Water Level Indicating Device? Steel Structures Meet AWWA Standard? Down-Turned Smooth-Nozzle Sample Tap? |  |  |  |  |  | Yes No Yes No Yes No Yes No Yes No Yes No |  |  |

WATER SUPPLY FINISHED

WATER STORAGE

2 of 2

| PRESSURE TANKS | Water Sight Glass? Automatic or Manual Air Blow Off? Pressure Switch For Pumps? Means for Adding Air? If Air Compressor, Give Capacity: CFM @ PSI |  |  |  |  | Yes No Yes No Yes No Yes No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TREATMENT PLANT STORAGE (clearwells only) |  |  |  | Minimum Two Clearwell Compartments Provided? |  | Yes No |  |
| Disinfection Method: (include chlorine dosage and retention time, including calculations) |  | NSF Sodium Hypochlorite Solution , 3 ppm, 48 minutes contact time -- 30 persons, 25 gpp, 12 hour operating time |  |  |  |  | Testing Yes No |
| PIPING |  | Influent: |  | 1" ( diameter-inches) | pvc (type of pipe) |  |  |
|  |  | Effluent: |  | 1" (diameter-inches) | pvc (type of pipe) |  |  |
| LOCATIONAL INFORMATION |  |  | Coordinates: Latitude 30°17’16.0”N Longitude 89°43’53.0”W OR Latitude 00. 00000°N Longitude 00. 00000°W |  |  |  |  |
|  |  |  | Geographic Datum: NAD83 WGS84 NAD27 |  |  |  |  |
|  |  |  | Collection Method: GPS — DGPS/WAAS enabled? Yes No — Horizontal Accuracy? meters Map Specify: Scale: |  |  |  |  |

WATER DISTRIBUTION SYSTEM

| Project: | Southern Comfort Lounge Water Supply |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: | Brian A. Mistich |  |  |  |  |  |  |  |  |  |
| Date: | 7/15/2015 |  |  |  |  |  |  |  |  |  |
| General Scope of Project: | Water Supply for a Lounge |  |  |  |  |  |  |  |  |  |
| ## PIPES | Material: (specify ASTM standard, dimension ratio-DR, AWWA Standard, and pressure class) |  | SDR 26 PVC |  |  |  |  |  |  | AWWA/NSF Approved? Yes No |
|  | Size: (Min 3” water main. Min 6” water main for fire protection. Water mains proposed with less than 3” diameter require justification with hydraulic analysis and future water use considerations provided and will only be allowed in special circumstances) |  |  |  |  |  | 2" Water well, 2" delivery line |  |  |  |
| JOINTS & MATERIALS: | Glue Joints |  |  |  |  |  |  |  |  |  |
|  | PVC |  |  |  |  |  |  |  |  |  |
| ## LAYOUT | Valve Spacing: |  |  | n/a |  |  |  |  |  |  |
|  | Means of Flushing Dead Ends? |  |  |  |  |  |  | Yes No |  |  |
|  | Number of Surface Water Crossings/Encounters? |  |  |  |  | 0 |  |  |  |  |
|  | Location with Respect to Sewers: |  |  |  | Maintain 18” Minimum Vertical Clearance @ Crossings? |  |  |  | Yes No |  |
|  |  |  |  |  | Maintain 6’ Minimum Horizontal Clearance? Yes No |  |  |  |  |  |
| Normal Operating Pressure: |  |  | 38 psi |  |  |  |  |  |  |  |
| Minimum System Pressure: |  |  | 25 psi |  |  |  |  |  |  |  |
| DISINFECTION METHOD (include chlorine dosage and Retention time): | NSF Sodium Hypochlorite Solution , 3 ppm, 48 minutes contact time |  |  |  |  |  |  |  |  |  |
| Owned and Operated By: (include name and address) | Mr. Raymond B. Williams 64491 Hwy 434 Lacombe, LA 70445 |  |  |  |  |  |  |  |  |  |
| NAME OF CERTIFIED OPERATOR: |  | Kerry Craig, #44512 |  |  |  |  |  |  |  |  |
| ADDITIONAL COMMENTS: | This is an existing system that has served the lounge for over 20 years |  |  |  |  |  |  |  |  |  |

DISINFECTION

| Project: | Southern Comfort Lounge |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: | Brian A. Mistich |  |  |  |  |  |  |
| Date: | 7/15/2015 |  |  |  |  |  |  |
| General Scope of Project: |  | Water Supply for a Lounge |  |  |  |  |  |
| Site Location: |  | 2209 Gause Blvd East, Slidell, La |  |  |  |  |  |
| TYPE OF DISINFECTION: |  | Chlorine: Gas Solution |  | Ammonia: Gas Ammonium Sulfate (solution) Ammonium Hydroxide (Aqua Ammonia) |  |  |  |
|  |  | Other (please explain): |  |  |  |  |  |
| FEEDERS/PUMPS: |  | # of Feeders/Pumps (2 minimum): |  |  |  | 1 active, 1 stanby |  |
|  |  | Type: | positive displacement |  |  |  |  |
| GENERAL: |  | Standby Equipment? Stored in Areas Not in Direct Sunlight? Vented to Outside? Enough Space for 30 Days Storage? |  |  |  |  | Yes No Yes No Yes No Yes No |
| STORAGE OF CHLORINE GAS: |  | Chlorine Storage & Feed System Building Separated? Doors Open Outward? Shatter-Resistant Inspection Windows? Fan/Light Switches Located Outside? Air Inlet Near Ceiling? Vent Fan Near Floor? Cylinders Restrained in Position? Weighing Scales? |  |  |  |  | Yes No Yes No Yes No Yes No Yes No Yes No Yes No Yes No |
| STORAGE OF AMMONIA GAS: |  | Ammonia Storage & Feed System Building Separated? Fan/Light Switches Located Outside? Air Inlet Near Ceiling? Vent Fan Near Floor with Elevated Intake? Leak Detection Systems in all Areas Through Which Ammonia is Piped? |  |  |  |  | Yes No Yes No Yes No Yes No Yes No |

LIFT STATION (S)

| Project: |  | n/a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General Scope of Project: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## PUMPS |  | # per Station: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Type: |  |  |  |  |  |  |  |  |  |  |  |  |  | Power: |  |  |
|  |  | Capacity (GPM): |  |  |  |  |  |  |  |  |  |  |  |  |  | @ TDH (FT) |  |  |
|  |  | Pump Line Sizes and Type |  |  |  |  |  | Suction Line: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Discharge Line (3” min. diameter without grinder pumps; 1 ¼” min. diameter with grinder pumps): |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Common Line: |  |  |  |  |  |  |  |  |  |  |
|  |  | Max. Solids Passage (2 ½” min.): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Gate Valve on Suction? Yes No |  |  |  |  |  |  |  |  |  |  |  | Gate Valve and Check Valves on Discharge? Yes No |  |  |  |  |
| ## WET WELL | Detention/Design flow (in minutes – 30 min maximum): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Pump Cycle Time: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Volume (low water to lead pump on): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Diameter: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bottom Elevation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Invert of Influent: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Floor Slope: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Access Cover Diameter: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Vented and Screened? Yes No |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FORCE MAIN |  | Size (3 inch min. diameter without grinder pumps; 1 ¼ inch diameter with grinder pumps): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Material (specify standard and standard dimension ratio-SDR: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Velocity (in fps – 2 fps minimum): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lift Station Cover Construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Alarm Systems: |  |  | Visual: |  |  | Yes No |  |  |  |  |  |  |  |  | Telemetry: |  | Yes No |  |
|  |  |  | Audible: |  |  | Yes No |  |  |  |  |  |  |  |  |  |  |  |  |

# EXTENDED AERATION SEWAGE

# TREATMENT FACILITY

1 of 3

| Project: | n/a |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Water Well within 100’? Yes No |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General Scope of Project: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Design Average Flow: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BOD5 Loading (in lbs of BOD5 per day): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Max. # of Lots or Population at Maximum Capacity: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Initial # of Lots (or population): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Industrial Waste: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Design Effluent Limits: |  |  |  |  | BOD5: |  |  |  |  | TSS: |  |  |  |  | NH3N: |  |
| RECEIVING STREAM: (provide complete path from outfall to first perennial non–intermittent waterway in the path of the projected outfall.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Plant Manufacturer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Plant Model #: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Materials of Construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## AERATION TANK |  | Volume: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Retention Time (24 Hour Min): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | BOD5 Loading: (lb per 1000 CF, 12.5 max.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Screen or Communutor? |  |  |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| FINAL CLARIFIER |  | Surface Area: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Surface Loading: (extended aeration plants 1000 gpd/ft2 @ peak hourly flow max loading) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Volume: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Scum Baffle: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Skimmer Through: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Weir Length (ft): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Weir Loading: (at peak hourly flow Plant ≤ 1mgd has 20,000 gpd/ft max load Plant > 1mgd has 30,000 gpd/ft max load) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### NAME OF CERTIFIED OPERATOR: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

# EXTENDED AERATION SEWAGE

# TREATMENT FACILITY

2 of 3

| ## AIR SUPPLY | # of Blowers (2 minimum): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Capacity of Each (SCFM): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SLUDGE RETURN |  |  | Method: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Maximum Flow (GPM): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Maximum Percent (% of DAF): |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SLUDGE DRYING BEDS |  | Number of Beds: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Area of Each Bed: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Total Area: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Area per Capita: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Gravel Layer Depth: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Sizes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Sand Depth: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Under-drain Size: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Freeboard Above Sand: |  |  |  |  |  |  |  |  |  |  |  |  |  | ## Splash Plate? Yes No |
|  |  | Effluent To: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SLUDGE LAGOONS |  | Number of Lagoons: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Maximum Depth: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Free Board: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Volume of Each Lagoon: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Volume of Each Lagoon per Capita: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Pump: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Piping Material: |  |  |  |  |  |  |  |  |  |  |  |  | Size: |  |
|  |  | Effluent To: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| OTHER SLUDGE DISPOSAL METHODS Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

# EXTENDED AERATION SEWAGE

# TREATMENT FACILITY

3 of 3

| ## CHLORINATION |  | Number: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Gas or Hypo: |  |  |  |  |  |  |  |  |  |
|  |  | Capacity (lb per 24 hrs): |  |  |  |  |  |  |  |  |  |
|  |  | Test Kit: |  |  |  |  |  |  |  |  |  |
|  |  | Location: |  |  |  |  |  |  |  |  |  |
|  |  | Ventilation: |  |  |  |  |  |  |  |  |  |
| CHLORINE CONTACT CHAMBER |  | Inside Dimensions |  |  | Length: |  |  |  |  |  |  |
|  |  |  |  |  | Width: |  |  |  |  |  |  |
|  |  |  |  |  | Operating Depth: |  |  |  |  |  |  |
|  |  | Capacity (gal): |  |  |  |  |  |  |  |  |  |
|  |  | Retention Time: (15 minute minimum @ peak hourly flow or maximum rate of pumping) |  |  |  |  |  |  |  |  |  |
|  |  | Over-and-Under or End-Around Baffles? Yes No |  |  |  |  |  |  |  | Scum Baffles? Yes No |  |
| ADDITIONAL DETATILS | Power Supply (Dual)? Yes No |  |  |  |  | Washdown Facility? Yes No |  |  | Backflow Prevention? Yes No |  |  |
|  |  |  |  |  |  |  |  |  | Type: |  |  |
|  | Facility Fenced? Yes No |  |  |  |  | ### Gates Locked? Yes No |  |  | Access Road? Yes No |  |  |
| Copy of DEQ Administrative Completeness Determination Letter and Response to Request for Preliminary Determination or Discharge Permit attached? |  |  |  |  |  |  |  |  |  |  | Yes No |
| ADDITIONAL COMMENTS |  |  |  |  |  |  |  |  |  |  |  |
| LOCATIONAL INFORMATION |  |  |  | Coordinates: Latitude 00°00’00.0”N Longitude 00°00’00.0”W OR Latitude 00. 00000°N Longitude 00. 00000°W |  |  |  |  |  |  |  |
|  |  |  |  | Geographic Datum: NAD83 WGS84 NAD27 |  |  |  |  |  |  |  |
|  |  |  |  | Collection Method: GPS — DGPS/WAAS enabled? Yes No — Horizontal Accuracy? meters Map Specify: Scale: |  |  |  |  |  |  |  |

OXIDATION POND

1 of 2

| Project: | n/a |  |  |  |  |  |  |  |  |  |  |  | Water Well within 100’? Yes No |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineer: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Site Location: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Industrial Waste: |  | Yes No |  |  |  |  | (If yes, list quantity and strength) |  |  |  |  |  |  |
| Design Average Capacity (lb BOD5 per day): |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Max # of Lots (or Population at Maximum Capacity): |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Initial # of Lots (or Population): |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Receiving Stream: (provide complete path from outfall to first perennial non-intermittent waterway in the path of the projected outfall) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1ST CELL | Influent Line |  | Material: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Size: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Depth of Discharge: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Location: |  |  |  |  |  |  |  |  |  |  |
|  | Levee |  | Interior Slope: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Exterior Slope: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Freeboard: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Crown Width: |  |  |  |  |  |  |  |  |  |  |
|  | Water Surface Area Provided: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Operating Depth: |  |  |  |  |  |  |  |  |  |  |  |  |
| 2ND & 3RD CELLS | ### Crossover Lines |  | Material: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Size: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ### Depth Liquid Drawn From: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ### Location: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ### Water Surface Area Provided: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ### Operating Depth: |  |  |  |  |  |  |  |  |  |  |
|  | ### Effluent Line |  | Material: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Size: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Depth Liquid Drawn From: |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Variable Depth: |  |  |  |  |  |  |  |  |  |  |

OXIDATION POND

2 of 2

| CHLORINE CONTACT CHAMBER | Inside Dimensions |  |  | Length: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Width: |  |  |  |  |  |  |
|  |  |  |  | Operating Depth: |  |  |  |  |  |  |
|  | Capacity (gal): |  |  |  |  |  |  |  |  |  |
|  | Retention Time: (15 minute minimum @ peak hourly flow or maximum rate of pumping) |  |  |  |  |  |  |  |  |  |
|  | Over-and-Under or End-Around Baffles? Yes No |  |  |  |  |  |  |  | Scum Baffles? Yes No |  |
| ADDITIONAL DETATILS | Washdown Facility? Yes No |  |  |  |  | Backflow Prevention? Yes No |  |  |  |  |
|  |  |  |  |  |  | Type: |  |  |  |  |
|  | Facility Fenced? Yes No |  |  |  | ### Gates Locked? Yes No |  |  | Access Road? Yes No |  |  |
| Copy of DEQ Administrative Completeness Determination Letter or Discharge Permit attached? |  |  |  |  |  |  |  |  |  | Yes No |
| ADDITIONAL COMMENTS |  |  |  |  |  |  |  |  |  |  |
| LOCATIONAL INFORMATION |  |  | Coordinates: Latitude 00°00’00.0”N Longitude 00°00’00.0”W OR Latitude 00. 00000°N Longitude 00. 00000°W |  |  |  |  |  |  |  |
|  |  |  | Geographic Datum: NAD83 WGS84 NAD27 |  |  |  |  |  |  |  |
|  |  |  | Collection Method: GPS — DGPS/WAAS enabled? Yes No — Horizontal Accuracy? meters Map Specify: Scale: |  |  |  |  |  |  |  |

CERTIFICATION OF CONSTRUCTION

Date: ___________________

Project Name: ______________________________________

______________________________________

______________________________________

______________________________________

Permit Number: ______________________________

I hereby certify that construction for the above referenced project has been completed in accordance with the plans and specifications approved by your office in your letter dated __________________________. The facility is now ready for operation.

Sincerely,

_________________________________	          _________________________________

Engineer of Record (Seal & Signature)	                      Contractor