Project HVAC Heat Load Calculations for Residence

ZONE #1 (Sensible Heat Loads)

Zone Specs : 1,400 s.f.; Exterior Wall = 158 l.f.; Exterior Wall Height = 10 ft; Floor on Piers

BTUh gain for East/West Double Pane Glass

3 ea x 2.67’ x 4.33’ x 95  (Load Factor) = 	3,295 BTUh

1 ea x 2’ x 4’ x 95 (Load Factor) = 		   760 BTUh

1 ea x 3’ x 5’ x 95 (Load Factor) = 		1,425 BTUh

BTUh gain for South Double Pane Glass

4 ea x 3 x 5 x 70 (Load Factor) = 		4,714 BTUh

1 ea x 2’ x 3.67’ x 70 (Load Factor) =

BTUh gain for North Double Pane Glass

5 x 3 x 5 x 20 (Load Factor) = 		1,500 BTUh

BTUh gain for Exterior Wall, Wood Construction R-11 & Gypsum

158 l.f. x 10 ft x 2.6 (Load Factor) = 		4,108 BTUh

BTUh gain for Ceiling with  6"  R-19

1,400 s.f. x 5.2 (Load Factor) = 		7,280 BTUh

BTUh gain for Floor Above Grade with  R-11

1,400 s.f. x 1.7 (Load Factor) = 		2,380 BTUh

BTUh gain for Occupants

3 x 500 (Load Factor) = 			1,500 BTUh

BTUh gain for Lighting

1,400 s.f. x 2.5 (Load Factor) = 		3,500 BTUh

BTUh gain for HVAC Ducts out of Conditioned Space

45 s.f. x 2.0  (Load Factor) = 			      90 BTUh

BTUh gain for Appliances

5,000 BTUh

ZONE #1 Total Sensible Heat Loads = 			35,552 BTUh

ZONE #1 (Latent Heat Loads)

BTUh gain for 84 cfm Fresh Air to AHU; 95 Deg outside temp, 74 Deg inside temp; 100% Humidity

cfm x Load Factor (Normal Humidity = 1.08) x tRise

84 cfm x 1.1 x (95 - 74) = 			1,940 BTUh

BTUh gain for 10 cfm Fresh Air per exterior door; 95 Deg outside temp, 74 Deg inside temp; 100% Humidity

cfm x Load Factor (Normal Humidity = 1.08) x tRise

20 cfm x 1.1 x (95 - 74) = 			     462 BTUh

ZONE #1 Total Latent Heat Loads = 			2,402 BTUh