ST. TAMMANY PARISH SCHOOL BOARD

SALMEN HIGH SCHOOL

NEW PRESS BOX

SLIDELL LA 



Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260526
GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

NFPA 70 and IEEE C2 include basic grounding requirements for electrical safety. This Section supplements those requirements with additional grounding requirements and with optional grounding methods and materials for both power and electronic systems that go beyond basic minimum safety requirements.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes grounding and bonding systems and equipment.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, provide products by one of the following available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

1. Burndy; Part of Hubbell Electrical Systems.

2. Dossert; AFL Telecommunications LLC.

3. ERICO International Corporation.

4. Fushi Copperweld Inc.

5. Galvan Industries, Inc.; Electrical Products Division, LLC.

6. Harger Lightning and Grounding.

7. ILSCO.

8. O-Z/Gedney; A Brand of the EGS Electrical Group.

9. Robbins Lightning, Inc.

10. Siemens Power Transmission & Distribution, Inc.

2.2 SYSTEM DESCRIPTION

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with UL 467 for grounding and bonding materials and equipment.

2.3 CONDUCTORS

Retain "Insulated Conductors" Paragraph below to require one of the two preferred conductor materials permitted by NFPA 70; delete to allow Contractor to use any material that complies with Code. See "Grounding Products" Article in the Evaluations for discussion on alternative materials.

A. Insulated Conductors: Copper wire or cable insulated for 600 V unless otherwise required by applicable Code or authorities having jurisdiction.

B. Bare Copper Conductors:

1. Solid Conductors: ASTM B 3.

2. Stranded Conductors: ASTM B 8.

3. Tinned Conductors: ASTM B 33.

Sizes and types of conductors in four subparagraphs below are typical examples. 28-kcmil bonding cable in "Bonding Cable" Subparagraph below is slightly larger than No. 6 AWG.

4. Bonding Cable: 28 kcmil, 14 strands of No. 17 AWG conductor, 1/4 inch in diameter.

5. Bonding Conductor: No. 4 or No. 6 AWG, stranded conductor.

6. Bonding Jumper: Copper tape, braided conductors terminated with copper ferrules; 1-5/8 inches wide and 1/16 inch thick.

7. Tinned Bonding Jumper: Tinned-copper tape, braided conductors terminated with copper ferrules; 1-5/8 inches wide and 1/16 inch thick.

2.4 CONNECTORS

A. Listed and labeled by an NRTL acceptable to authorities having jurisdiction for applications in which used and for specific types, sizes, and combinations of conductors and other items connected.

B. Bolted Connectors for Conductors and Pipes: Copper or copper alloy.

C. Welded Connectors: Exothermic-welding kits of types recommended by kit manufacturer for materials being joined and installation conditions.

D. Bus-Bar Connectors: Mechanical type, cast silicon bronze, solderless compression or exothermic-type wire terminals, and long-barrel, two-bolt connection to ground bus bar.

2.5 GROUNDING ELECTRODES

Grounding electrodes include ground rods, metal underground water pipes, metal building frames, concrete-encased electrodes, and pipe and plate electrodes. Retain "Applications" and "Installation" articles to specify where these items are required; coordinate with Drawings.

Copper-clad steel ground rods are the most common grounding electrode. See Evaluations for discussion on alternative materials. Sectional rods are used when electrodes longer than 10 feet (3 m) are required.

A. Ground Rods: Copper-clad steel; 3/4 inch by 10 feet.

PART 3 -  EXECUTION

3.1 APPLICATIONS

A. Conductors: Install solid conductor for No. 8 AWG and smaller, and stranded conductors for No. 6 AWG and larger unless otherwise indicated.

Coordinate "Underground Grounding Conductors" Paragraph below with Drawings and with Section 260543 "Underground Ducts and Raceways for Electrical Systems."

B. Underground Grounding Conductors: Install bare copper conductor, No. 2/0 AWG minimum.

1. Bury at least 24 inches below grade.

C. Conductor Terminations and Connections:

1. Pipe and Equipment Grounding Conductor Terminations: Bolted connectors.

2. Underground Connections: Welded connectors except at test wells and as otherwise indicated.

3. Connections to Ground Rods at Test Wells: Bolted connectors.

4. Connections to Structural Steel: Welded connectors.

3.2 GROUNDING AT THE SERVICE
A. Equipment grounding conductors and grounding electrode conductors shall be connected to the ground bus. Install a main bonding jumper between the neutral and ground buses.

3.3 GROUNDING OVERHEAD LINES

A. Comply with IEEE C2 grounding requirements.

B. Install 2 parallel ground rods.

C. Drive ground rods until tops are 12 inches below finished grade in undisturbed earth.

D. Ground-Rod Connections:  Install bolted connectors for underground connections and connections to rods.

E. Lightning Arrester Grounding Conductors:  Separate from other grounding conductors.

F. Secondary Neutral and Transformer Enclosure.  Interconnect and connect to grounding conductor.

G. Protect grounding conductors running on surface of wood poles with molding extended from grade level up to and through communication service and transformer spaces.

3.4 GROUNDING UNDERGROUND DISTRIBUTION SYSTEM COMPONENTS

A. Comply with IEEE C2 grounding requirements.

Grounding practices of the local utility company may differ from requirements in "Grounding Manholes and Handholes," "Grounding Connections to Manhole Components," and "Pad-Mounted Transformers and Switches" paragraphs below. Although grounding specified in this article is not for the utility company's use and does not have to comply with its standards, it is possible the utility company may be requested to repair or maintain the line in the future. For this reason, it may be desirable to design some grounding features according to the utility company's standards. Utility companies, for economic reasons, often design to a standard lower than what is appropriate for Project requirements. Alternatively, because of their experience with conditions in their service area, utility companies may design to a higher standard than is required by Code. In addition to Project requirements, evaluate the local utility company's practices and revise paragraphs accordingly. This evaluation is particularly important if Project's underground lines connect with utility lines. Coordinate with Drawings and with Section 260543 "Underground Ducts and Raceways for Electrical Systems."

Retain and revise "Pad-Mounted Transformers and Switches" Paragraph below to exceed NFPA 70 requirements. If concrete pad is for equipment to be supplied by utility company, revise paragraph to comply with utility company's grounding standards or delete and detail on Drawings.

B. Pad-Mounted Transformers and Switches: Install two ground rods around the pad. Ground pad-mounted equipment and noncurrent-carrying metal items associated with substations by connecting them to underground cable and grounding electrodes. Install tinned-copper conductor not less than No. 2 AWG for taps to equipment grounding terminals.

3.5 EQUIPMENT GROUNDING

NFPA 70 permits two types of equipment grounding conductors: metallic raceway or cable sheath that encloses supply conductors, and a separate grounding conductor of insulated wire or cable installed with supply conductors. Installation of a separate insulated equipment grounding conductor provides an additional degree of safe operation when compared to relying on raceway or cable sheath for ground continuity. NFPA 70 requires separate insulated equipment grounding conductors in some situations and not in others. Retain and revise one of first two paragraphs below to require insulated equipment grounding conductors that exceed NFPA 70 requirements. Coordinate with Drawings.

A. Install insulated equipment grounding conductors with all feeders and branch circuits.

B. Install insulated equipment grounding conductors with the following items, in addition to those required by NFPA 70:

Retain applicable subparagraphs below.

1. Feeders and branch circuits.

2. Lighting circuits.

3. Receptacle circuits.

4. Single-phase motor and appliance branch circuits.

5. Three-phase motor and appliance branch circuits.

6. Flexible raceway runs.

7. Armored and metal-clad cable runs.

8. Busway Supply Circuits: Install insulated equipment grounding conductor from grounding bus in the switchgear, switchboard, or distribution panel to equipment grounding bar terminal on busway.

9. X-Ray Equipment Circuits: Install insulated equipment grounding conductor in circuits supplying x-ray equipment.

C. Air-Duct Equipment Circuits: Install insulated equipment grounding conductor to duct-mounted electrical devices operating at 120 V and more, including air cleaners, heaters, dampers, humidifiers, and other duct electrical equipment. Bond conductor to each unit and to air duct and connected metallic piping.

D. Water Heater, Heat-Tracing, and Antifrost Heating Cables: Install a separate insulated equipment grounding conductor to each electric water heater and heat-tracing cable. Bond conductor to heater units, piping, connected equipment, and components.

"Poles Supporting Outdoor Lighting Fixtures" Paragraph below may supplement equipment grounding conductor and may be in excess of NFPA 70 requirements. Retain if necessary and coordinate with Drawings.

E. Poles Supporting Outdoor Lighting Fixtures: Install grounding electrode and a separate insulated equipment grounding conductor in addition to grounding conductor installed with branch-circuit conductors.

See Evaluations for discussion of fence grounding.

F. Metallic Fences: Comply with requirements of IEEE C2.

1. Grounding Conductor: Bare copper, not less than No. 8 AWG.

2. Gates: Shall be bonded to the grounding conductor with a flexible bonding jumper.

3. Barbed Wire: Strands shall be bonded to the grounding conductor.

3.6 INSTALLATION

A. Grounding Conductors: Route along shortest and straightest paths possible unless otherwise indicated or required by Code. Avoid obstructing access or placing conductors where they may be subjected to strain, impact, or damage.

B. Ground Bonding Common with Lightning Protection System: Comply with NFPA 780 and UL 96 when interconnecting with lightning protection system. Bond electrical power system ground directly to lightning protection system grounding conductor at closest point to electrical service grounding electrode. Use bonding conductor sized same as system grounding electrode conductor, and install in conduit.

C. Ground Rods: Drive rods until tops are 2 inches  below finished floor or final grade unless otherwise indicated.

1. Interconnect ground rods with grounding electrode conductor below grade and as otherwise indicated. Make connections without exposing steel or damaging coating if any.

Retain subparagraph below if grounding installation requirements are not detailed on Drawings. Subparagraph exceeds NFPA 70 requirements.

2. For grounding electrode system, install at least three  rods spaced at least one-rod length from each other and located at least the same distance from other grounding electrodes, and connect to the service grounding electrode conductor.

Retain "Test Wells" Paragraph below to require test wells; delete if detailed on Drawings.

D. Test Wells: Ground rod driven through drilled hole in bottom of handhole and shall be at least 12 inches deep, with cover.

1. Test Wells: Install at least one test well for each service unless otherwise indicated. Install at the ground rod electrically closest to service entrance. Set top of test well flush with finished grade or floor.

E. Bonding Straps and Jumpers: Install in locations accessible for inspection and maintenance except where routed through short lengths of conduit.

1. Bonding to Structure: Bond straps directly to basic structure, taking care not to penetrate any adjacent parts.

2. Bonding to Equipment Mounted on Vibration Isolation Hangers and Supports: Install bonding so vibration is not transmitted to rigidly mounted equipment.

3. Use exothermic-welded connectors for outdoor locations; if a disconnect-type connection is required, use a bolted clamp.

If connections specified in "Grounding and Bonding for Piping" Paragraph below circumvent dielectric fittings intended to isolate interior piping systems from ground, other action may be necessary to prevent electrolytic corrosion.

F. Grounding and Bonding for Piping:

1. Metal Water Service Pipe: Install insulated copper grounding conductors, in conduit, from building's main service equipment, or grounding bus, to main metal water service entrances to building. Connect grounding conductors to main metal water service pipes; use a bolted clamp connector or bolt a lug-type connector to a pipe flange by using one of the lug bolts of the flange. Where a dielectric main water fitting is installed, connect grounding conductor on street side of fitting. Bond metal grounding conductor conduit or sleeve to conductor at each end.

2. Water Meter Piping: Use braided-type bonding jumpers to electrically bypass water meters. Connect to pipe with a bolted connector.

3. Bond each aboveground portion of gas piping system downstream from equipment shutoff valve.

3.7 FIELD QUALITY CONTROL

A. Perform tests and inspections. Inspect physical and mechanical condition. Verify tightness of accessible, bolted, electrical connections with a calibrated torque wrench according to manufacturer's written instructions.

END OF SECTION 260526
	GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS
	260526 - 1



