## Sheet1
HVAC MECHANICAL ESTIMATE _ BOYET JUNIOR HIGH SCHOOL
TASK | DESCRIPTION | EQUIPMENT |  | LABOR |  |  | MATERIAL |  | REMARKS
|  | DESCRIPTION | $, TOTAL | CREW | TOTAL LABOR HOURS | $, TOTAL | DESCRIPTION | $, TOTAL
Demolition | Demolition, air handling unit "A" (15 ton in trusses, 30 ft above grade) | Manlift | 420 | 3 sht. mtl. | 24 | 1440 |  |  | Approximately 30 feet above grade
| Demolition, air handling unit "B" (15 ton in trusses, 30 ft above grade) | Manlift | 420 | 3 sht. mtl. | 24 | 1440 |  |  | Approximately 30 feet above grade
| Demolition, condenser "A", on grade | Forklift | 210 | 2 sht. mtl. | 6 | 240 |  |  | Demolish exist. condenser
| Demolition, condenser "B" on grade | Forklift | 210 | 2 sht. mtl. | 6 | 240 |  |  | Demolish exist. condenser
| Demolition, air handling unit (5 ton fan coil in gym) | Scafolding | 100 | 2 sht. mtl. | 3 | 120
| Demolition, condensing unit (5 ton gym roof) | Forklift | 120 | 2 sht. mtl. | 2 | 80
| Demolition, Ductless Mini-Split (1.5 ton Food Services @ Entrance) | Ladder | 0 | 2 sht. mtl. | 4 | 160 |  |  | Demolish exist. Fan coil unit
Structural | Concrete Pad for RTU#1 | [5 empty] | Concrete Pad | 2000
Electrical | RTU#1 | Ladder | 0 |  | 17.838 | 1079.199 | Materials | 3863.73
| RTU#2 | Scaffolding | 200 |  | 68.524 | 4145.702 | Materials | 8397.705
| AHU#1 | Scaffolding | 200 |  | 55.6624 | 3367.5752 | Materials | 2858.9325
| AHU#2 | Scaffolding | 200 |  | 34.6348 | 2095.4054 | Materials | 2070.195
| Mini-Split | Ladder | 0 |  | 17.3 | 1046.65 | Materials | 1657.05
Construction | Install 15 ton packaged RTU#1 on Ground | Forklift | 210 | 2 sht. mtl. | 20 | 1000 | 15 Ton packaged DX unit, 208-3 phase, 36 kW Heat | 18300 | Install on grade with duct routed to overherad diffusers near roof.
| Install 15 ton packaged RTU#2 on Ground | Forklift | 210 | 2 sht. mtl. | 20 | 1000 | 15 Ton packaged DX unit, 208-3 phase, 36 kW Heat | 18300 | Install on grade with duct routed to overherad diffusers near roof.
| Ductwork for RTU#1 | Manlift | 210 | 3 sht. mtl. | 72 | 3960 | 20" x 40" duct, 40 ft. long | 2600 | 2,500 Lb. galvanized sheetmetal
| Ductwork for RTU#2 | Manlift | 210 | 3 sht. mtl. | 72 | 3960 | 20" x 40" duct, 40 ft. long | 2600 | 2,500 Lb. galvanized sheetmetal
| Duct insulation, interior liner, both units | Manlift | 210 | 2 sht. mtl. | 16 | 880 | Duct insulation, 1600 Sq. Ft. | 2240 | 1-1/2" thk duct wrap with FSK & weather jacket
| Install S/A & R/A grilles in upper wall - both 15 ton units | Manlift | 210 | 2 sht. mtl. | 16 | 960 | Sidewall registers w/ adjustable vanes | 820 | Painted steel to match wall
| Fabricate & install ductwork for 5 ton split DX air handling unit | Scaffolding | 200 | 2 sht. mtl. | 40 | 1600 | Fabricate & install 16" x 16" metal duct, 50 ft. long | 300 | 280 Lb. galvanized sheetmetal
| Fabricate & install ductwork for 5 ton split DX air handling unit | Scaffolding | 200 | 2 sht. mtl. | 40 | 1600 | Fabricate & install 16" x 16" metal duct, 50 ft. long | 300 | 280 Lb. galvanized sheetmetal
| Install 5 ton split DX AHU #1 | Scafolding | 100 | 2 sht. mtl. | 12 | 600 | 5 Ton split system DX | 4500 | Including 5 ton condenser
| Install 5 ton split DX AHU #2 | Scafolding | 100 | 2 sht. mtl. | 12 | 600 | 5 Ton split system DX | 4500 | Including 5 ton condenser
| Install ductwork for 5 ton split DX | Scaffolding | 200 | 2 sht. mtl. | 40 | 2000 | 16" x 16" metal duct, 50 ft. long | 300 | 280 Lb. galvanized sheetmetal
| Install ductwork for 5 ton split DX | Scaffolding | 200 | 2 sht. mtl. | 40 | 2000 | 16" x 16" metal duct, 50 ft. long | 300 | 280 Lb. galvanized sheetmetal
| Duct insulation, liner | Ladder | 0 | 2 sht. mtl. | 12 | 600 | Duct insulation, 300 Sq. Ft. | 420 | 1-1/2" thk duct wrap with FSK vapor barrier
| Duct insulation, liner | Ladder | 0 | 2 sht. mtl. | 12 | 600 | Duct insulation, 300 Sq. Ft. | 420 | 1-1/2" thk duct wrap with FSK vapor barrier
| S/A and R/A grilles for 5 ton DX unit | Ladder | 0 | 1 sht. mtl. | 8 | 400 | 16" x 10" registers | 390 | w/ adjustable vanes
| S/A and R/A grilles for 5 ton DX unit | Ladder | 0 | 1 sht. mtl. | 8 | 400 | 16" x 10" registers | 390 | w/ adjustable vanes
| 30,000 BTUH mini-split system with ceiling cassette for front entry lobby | Ladder | 0 | 2 sht. mtl. | 24 | 1200 | 30,000 BTUH mini-split | 4650 | New installation
| 18,000 BTUH mini-split system for area adjacent to front entry lobby | Ladder | 0 | 2 sht. mtl. | 16 | 800 | 18,000 BTUH mini-split | 2700 | Replace in kind
| 16" side wall exhaust fan, 1500 CFM | Ladder | 0 | 1 elect, 1 sht. mtl. | 16 | 800 | 16" side wall exhaust fan | 650 | w/ exterior rain hood & shutter
| Grille balancing | Ladder | 0 | 1 sht. mtl. | 6 | 300 | Air balance | 0 | balance to within 10% of design
| Equipment Subtotal ($) : |  | 4340 |  | Labor Subtotal ($): | 40714.5316 | Material Subtotal ($): | 85527.6125
[7 empty] | Overall Subtotal: | 130582.1441 | Equipment, labor & material
[7 empty] | Mobilization and demobilization | 5000
[7 empty] | Height/difficulty factor: | 3000
[7 empty] | Administartion: | 630
[7 empty] | Contingency (20%): | 26116.4288
[7 empty] | Permits & Fees (3%): | 3917.4643
[7 empty] | Bond (3%): | 3917.4643
[7 empty] | Tax (9%): | 11752.393
[7 empty] | Total: | 184915.8945

## Electrical
|  | Size | Length | Labor Hrs | Material/CLF | Labor/hr | Material Cost | Labor HRs
MiniSp | Wire | #6 | 400 | 1.2 | 81.75 | 60.5 | 49.05 | 4.8 | 2703.7
MiniSp | Conduit | 1" | 100 | 0.1 | 6.57 | 60.5 | 985.5 | 10
RTU#1 | Wire | 2/0 | 200 | 2.759 | 397.5 | 60.5 | 1192.5 | 5.518 | 4942.929
RTU#1 | Conduit | 2" | 40 | 0.133 | 14.55 | 60.5 | 8.73 | 5.32
AHU#2 | Wire | #4 | 720 | 1.509 | 129.75 | 60.5 | 1401.3 | 10.8648 | 4165.6004
AHU#2 | Conduit | 1.25" | 180 | 0.114 | 8.85 | 60.5 | 23.895 | 20.52
RTU#2 | Wire | 4/0 | 900 | 3.636 | 420 | 60.5 | 5670 | 32.724 | 12543.407
RTU#2 | Conduit | 2.5 | 180 | 0.16 | 24.15 | 60.5 | 65.205 | 28.8
AHU#1 | Wire | #2 | 1080 | 1.778 | 134 | 60.5 | 2170.8 | 19.2024 | 6226.5077
AHU#1 | Conduit | 1.5 | 270 | 0.123 | 10.65 | 60.5 | 43.1325 | 33.21
|  |  |  | Wire CLF = 100 FT |  | Conduit = LF
Disconnects
MiniSp | 40 Amp | 1 Phase |  | 2 | 350 | 60.5 | 525 | 2
RTU#1 | 150 Amp | 3 Phase |  | 6 | 875 | 60.5 | 1312.5 | 6
AHU#2 | 60 Amp | 1 Phase |  | 2.5 | 350 | 60.5 | 525 | 2.5
RTU#2 | 150 Amp | 3 Phase |  | 6 | 875 | 60.5 | 1312.5 | 6
AHU#1 | 60 Amp | 1 Phase |  | 2.5 | 350 | 60.5 | 525 | 2.5
Breakers
MiniSp | 40 Amp | 1 Phase |  | 0.5 | 65 | 60.5 | 97.5 | 0.5
RTU#1 | 150 Amp | 3 Phase |  | 1 | 900 | 60.5 | 1350 | 1
AHU#2 | 60 Amp | 1 Phase |  | 0.75 | 80 | 60.5 | 120 | 0.75
RTU#2 | 150 Amp | 3 Phase |  | 1 | 900 | 60.5 | 1350 | 1
AHU#1 | 60 Amp | 1 Phase |  | 0.75 | 80 | 60.5 | 120 | 0.75