|  | Submittal |
| --- | --- |

| Prepared For: Wisnor & Associates | Date: December 05, 2022 Job Name: Boyett Jr High School |
| --- | --- |

_____________________________________________________________________________________________

Trane U.S. Inc. is pleased to provide the following submittal for your review and approval.

# Product Summary

| Qty | Product |
| --- | --- |
| 2 | PREC |
| 1 | Split System Air Conditioning Units (Small) |

_____________________________________________________________________________________________

| Kimberly Fricke Trane U.S. Inc. 4013 N Interstate 10 Service Rd W Metairie, LA 70002 Office Phone: (504) 733-6789 | The attached information describes the equipment we propose to furnish for this project and is submitted for your approval. Submittal acceptance and return is a critical step, so please ensure submittals are returned with approval to release to production within 14 days of submittal date. Product performance and submittal data is valid for a period of 6 months from the date of submittal generation. If six months or more has elapsed between submittal generation and equipment release, the product performance and submittal data will need to be verified. It is the customer’s responsibility to obtain such verification. |
| --- | --- |

Table of Contents

Product Summary	1

PREC (Item A1)	3

Tag Data	3

Product Data	3

Performance Data	4

Mechanical Specifications	6

Dimensional Drawings	8

Weight, Clearance & Rigging	12

Accessory	13

Split System Air Conditioning Units (Small) (Item B1)	14

Tag Data	14

Product Data	14

Performance Data	15

Mechanical Specifications	16

Dimensional Drawings	17

Weight, Clearance & Rigging	21

Field Installed Options - Part/Order Number Summary	22

PREC	22

Split System Air Conditioning Units (Small)	22

## Tag Data - PREC (Qty: 2)

| Item | Tag(s) | Qty | Description | Model Number |
| --- | --- | --- | --- | --- |
| A1 | RTU-1, RTU-2 | 2 | 6- 25 Ton PKGD Precedent Unitary Rooftop | TSJ180A3S00**000000000000000000000000000 |

Product Data - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

DX Cooling

Standard Efficiency

R-410A

15 Ton

208-230/60/3

Symbio 700

Motorized outside damper 0-50% (Field Installed)

Horizontal Conversion Panel (Field Installed)

Performance Data - 6- 25 Ton PKGD Precedent Unitary Rooftops (PREC)

| Tags | RTU-1, RTU-2 |
| --- | --- |
| Cooling Entering Dry Bulb (F) | 80.00 |
| Cooling Entering Wet Bulb (F) | 67.00 |
| Summer Ambient (F) | 95.00 |
| Entering Dry Bulb (in HGRH) (F) | 73.00 |
| Entering Wet Bulb (in HGRH) (F) | 64.00 |
| Ambient (In HGRH) (F) | 75.00 |
| Design Airflow (cfm) | 6000 |
| Airflow Application | Horizontal |
| Design ESP (in H2O) | 0.500 |
| Fan Pressurized (in H2O) | 0.540 |
| Design ESP + Component SP (in H2O) | 0.500 |
| Elevation (ft) | 0.00 |
| Gross Total Capacity (MBh) | 188.59 |
| Gross Sensible Capacity (MBh) | 146.26 |
| Gross Latent Capacity (MBh) | 42.34 |
| Net Total Capacity (MBh) | 184.56 |
| Net Sensible Capacity (MBh) | 142.22 |
| Net Sensible Heat Ratio (%) | 77.00 |
| Coil LAT DB (F) | 57.09 |
| Coil LAT WB (F) | 56.80 |
| Cooling Leaving Unit Dry Bulb (F) | 58.20 |
| Cooling Leaving Unit WB (F) | 57.24 |
| Fan Motor Heat (MBh) | 4.03 |
| Dew Point Temperature (F) | 56.64 |
| Refrigerant charge (HFC-410A) - Ckt 1 (lb) | 14.5 |
| Saturated Discharge Temperature (F) | 121.42 |
| Saturated Suction Temperature (F) | 51.15 |
| Heat Static Pressure Adj (in H2O) | 0.000 |
| Component SP Add (in H2O) | 0.000 |
| Max Available ESP (in H2O) | 2.000 |
| Supply Motor Horsepower (hp) | 3.100 |
| Supply Operating Horsepower (hp) | 1.280 |
| Supply RPM (rpm) | 1003 |
| Compressor Power (kW) | 12.86 |
| System Power (kW) | 16.96 |
| EER @ AHRI (Number) | 11.00 |
| IEER @ AHRI (Number) | 14.20 |
| MCA (A) | 78.00 |
| MOP (A) | 100.00 |
| Compressor 1 RLA (A) | 30.90 |
| Compressor 2 RLA (A) | 16.40 |
| Condenser Fan FLA (A) | 2.30 |
| Evaporator Fan FLA (A) | 8.80 |
| Height (ft) | 4.92 |
| Width (ft) | 7.25 |
| Length (ft) | 10.25 |
| Approx Configured Weight (lb) | 1820.0 |
| Approx Installed Weight (lb) | 1820.0 |
| Corner weight A (lb) | 611.0 |
| Corner Weight B (lb) | 447.0 |
| Corner Weight C (lb) | 322.0 |
| Corner Weight D (lb) | 440.0 |
| Center of Gravity - Length (ft) | 4.33 |
| Center of Gravity - Width (ft) | 3.00 |
| Ducted Discharge - 63 Hz (dB) | 80 |
| Ducted Discharge - 125 Hz (dB) | 79 |
| Ducted Discharge - 250 Hz (dB) | 73 |
| Ducted Discharge - 500 Hz (dB) | 67 |
| Ducted Discharge - 1 kHz (dB) | 62 |
| Ducted Discharge - 2 kHz (dB) | 57 |
| Ducted Discharge - 4 kHz (dB) | 55 |
| Ducted Discharge - 8 kHz (dB) | 53 |
| Ducted Inlet - 63 Hz (dB) | 81 |
| Ducted Inlet - 125 Hz (dB) | 74 |
| Ducted Inlet - 250 Hz (dB) | 69 |
| Ducted Inlet - 500 Hz (dB) | 62 |
| Ducted Inlet - 1 kHz (dB) | 56 |
| Ducted Inlet - 2 kHz (dB) | 55 |
| Ducted Inlet - 4 kHz (dB) | 56 |
| Ducted Inlet - 8 kHz (dB) | 52 |
| Outdoor Noise - 63 Hz (dB) | 84 |
| Outdoor Noise - 125 Hz (dB) | 91 |
| Outdoor Noise - 250 Hz (dB) | 95 |
| Outdoor Noise - 500 Hz (dB) | 93 |
| Outdoor Noise - 1 kHz (dB) | 89 |
| Outdoor Noise - 2 kHz (dB) | 85 |
| Outdoor Noise - 4 kHz (dB) | 82 |
| Outdoor Noise - 8 kHz (dB) | 76 |
| Acoustic Footnote 1 | Ducted Discharge and Ducted Inlet Sound in accordance with AHRI 260-2017 |
| Acoustic Footnote 2 | Outdoor Sound in accordance with AHRI 370-2015 |
| Heat pump heating ambient temperature (F) | 47.00 |
| Heat pump heating ambient relative humid (%) | 70.00 |
| Supply Fan Count (Number) | 2.00 |

Mechanical Specifications - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

General

- Packaged rooftop units cooling, heating capacities, and efficiencies are AHRI Certified within scope of AHRI Standard 210-240 for 6 to 25 Tons and ANSIZ21.47 and 10 CFR Part 431 pertaining to Commercial Warm Air Furnaces (all gas heating units).

-Convertible airflow.

-Symbio controls operating range is from 0-125 from factory; if designing for cooling mode operation below 40 deg F ambient temp, add low ambient kit to assure continuous and reliable operation.

-Factory assembled, internally wired, fully charged with R-410A, and 100 percent run tested to check cooling operation, fan and blower rotation, and control sequence before leaving the factory.

-Colored and numbered wiring internal to the unit for simplified identification.

-Units cULus listed and labeled, classified in accordance for Central Cooling Air Conditioners.

Casing

-Zinc coated, heavy gauge, galvanized steel.

-Weather resistant pre-painted metal with galvanized substrate.

-Meets ASTM B117, 672 hour salt spray test.

-Removable single side maintenance access panels.

-Lifting handles in maintenance access panels (can be removed and reinstalled by removing fasteners while providing a water and air tight seal).

-Exposed vertical panels and top covers in the indoor air section insulated with a cleanable foil-faced, fire-retardant permanent, odorless glass fiber material.

-Base pan shall have no penetrations within the perimeter of the curb other than the raised 1 inch high downflow supply/return openings to provide an added water integrity precaution, if the condensate drain backs up.

-Base of the unit insulated with 1/8 inch, foil-faced, closed-cell insulation.

-Unit base provisions for forklift and/or crane lifting on three sides of unit.

Hail Guards

-Provides condenser coil protection.

Microchannel Coils

-Optimal heat transfer performance due to flat, streamlined tubes with small ports, and metallurgical tube-to-fin bond.

-Reduce system refrigerant charge by up to 50% leading to better compressor reliability.

-Compact all-aluminum microchannel coils reduce the unit weight.

-Recyclable all aluminum coils All aluminium construction minimizes galvanic corrosion.

-Strong aluminum brazed structure provides better fin protection.

-Flat streamlined tubes more dust resistant and easy to clean.

-Coils leak tested at the factory to ensure the pressure integrity.

Compressors

-All units have direct-drive, hermetic, scroll type compressors with centrifugal type oil pumps.

-Suction gas-cooled motor with voltage utilization range of plus or minus 10 percent of unit nameplate voltage.

-Internal overloads standard with scroll compressors.

-Crankcase heaters are standard on all compressors.

-All units have dual compressors.

-Three stages of cooling available on 6 to 17.5 tons units and four stages of cooling available on 20 and 25 tons units.

Filters

Two inch standard filters shall be factory supplied on all units.

Frostat

-Utilized as a safety device.

-Opens to prevent freezing temperatures on evaporator coil.

-Temperature will need to rise to 50°F before closing.

-Utilized in low airflow or high outside air applications (cooling only).

Motorized Outside Air Damper

-Once set, when indoor fan starts, outdoor air dampers shall open to set position.

-When indoor fan shuts down, damper shall close to the full closed position.

Dimensional Drawings - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

Dimensional Drawings - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

Dimensional Drawings - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

Note:  Fan Curves are for TSJ/WSJ units.   For YSJ units, add additional static pressure for Gas Heat Exchanger (ref. RT-PRC098*, table 47)

Dimensional Drawings - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

Note:  Fan Curves are for TSJ/WSJ units.   For YSJ units, add additional static pressure for Gas Heat Exchanger (ref. RT-PRC098*, table 47)

Weight, Clearance & Rigging - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

Accessory - PREC

Item: A1  Qty: 2  Tag(s): RTU-1, RTU-2

## Tag Data - Split System Air Conditioning Units (Small) (Qty: 1)

| Item | Tag(s) | Qty | Description | Model Number |
| --- | --- | --- | --- | --- |
| B1 | AHU CU-1 | 1 | 1.5 - 5 Ton Unitary Split Systems (SSC) | 4TTR4060N10000*00000*TEM4B0C60S51S*********000**0000*0***000000000000000000000*0**0 |

Product Data - Split System Air Conditioning Units (Small)

Item: B1  Qty: 1  Tag(s): AHU CU-1

Split System Cooling Outdoor Unit

5 Ton Nominal Cooling Capacity

Major Design Sequence N

200 - 230 Volt 1 Phase 60 Hertz

Low cost

Multi-poise 4-way

Better, Retail replacement Mid EFF

Footprint - C

5 Ton air handler

Std Efficiency

5.0 ton airflow

208-230/1/60

Standard Coil

Brazed

7.21/9.60 kW Htr w/Ckt Brk 208/240/1 (Field Installed)

Performance Data - 1.5 - 5 Ton Unitary Split Systems (SSC)

| Tags | AHU CU-1 |
| --- | --- |
| Design clg EDB (F) | 80.00 |
| Design clg EWB (F) | 67.00 |
| Cooling outdoor DB (F) | 95.00 |
| Cooling EDB (F) | 80.00 |
| Cooling EWB (F) | 67.00 |
| Capacity @ AHRI (Btuh) | 56000.00 |
| Elevation (ft) | 0.00 |
| Clg net total capacity (Btuh) | 58446.00 |
| Clg net sensible capacity (Btuh) | 44191.00 |
| Clg net latent capacity (Btuh) | 14255.00 |
| Calc clg LDB (F) | 58.40 |
| Calc clg LWB (F) | 57.00 |
| SEER @ AHRI (btuh/watt) | 14.30 |
| EER @ AHRI (EER) | 11.7 |
| Cooling airflow (cfm) | 1925 |
| Min system airflow clg (cfm) | 1500 |
| Max system airflow clg (cfm) | 1925 |
| AHRI airflow (cfm) | 1505 |
| AHRI compressor power clg mode (W) | 4020.0 |
| AHRI condenser fan power clg mode (W) | 240.0 |
| AHRI supply fan power clg mode (W) | 526.0 |
| ASHRAE 90.1 S6.4.1 compliant | Yes |
| Heating airflow (cfm) | 1925 |
| Heating EDB (F) | 68.00 |
| 80 to 90 second blower off delay | Required |
| OD AHRI Model (Each) | -1.00 |
| ID AHRI Model (Each) | 9067887.00 |

Mechanical Specifications - Split System Air Conditioning Units (Small)

Item: B1  Qty: 1  Tag(s): AHU CU-1

4TTR4 - General

The Outdoor Units are fully charged from the factory for up to 15 feet of piping. This unit is designed to operate at outdoor ambient temperatures as high as 115F. Cooling capacities are matched with a wide selection of air handlers and furnace coils that are AHRI certified. The unit is certified to UL 1995. Exterior is designed for outdoor application.

4TTR4 - Casing

Unit casing is constructed of heavy gauge, G60 galvanized steel and painted with a weather resistant powder paint on all louvered panels and prepaint on all other panels. Corrosion and weatherproof CMBP-G30 base.

4TTR4 - Refrigerant Controls

Refrigeration system controls include condenser fan, compressor contactor and high pressure switch. High and low pressure controls are inherent to the compressor. A factory supplied liquid line drier is standard. Some models may require field installation.

4TTR4 - Compressor

The compressor features internal over temperature, pressure protection and total dipped hermetic motor. Other features include: Centrifugal oil pump and low vibration and noise.

4TTR4 - Condenser Coil

The outdoor coil provides low airflow resistance and efficient heat transfer. The coil is protected on all four sides by louvered panels.

4TTR4 - Low Ambient Cooling

As manufactured, this system has a cooling capacity to 55F. The addition of an evaporator defrost control permits operation to 40F. The addition of an evaporator defrost control with TXV permits low ambient cooling to 30F.

Dimensional Drawings - Split System Air Conditioning Units (Small)

Item: B1  Qty: 1  Tag(s): AHU CU-1

Dimensional Drawings - Split System Air Conditioning Units (Small)

Item: B1  Qty: 1  Tag(s): AHU CU-1

Dimensional Drawings - Split System Air Conditioning Units (Small)

Item: B1  Qty: 1  Tag(s): AHU CU-1

Dimensional Drawings - Split System Air Conditioning Units (Small)

Item: B1  Qty: 1  Tag(s): AHU CU-1

Weight, Clearance & Rigging - Split System Air Conditioning Units (Small)

Item: B1  Qty: 1  Tag(s): AHU CU-1

Field Installed Options - Part/Order Number Summary

This is a report to help you locate field installed options that arrive at the jobsite. This report provides part or order numbers for each field installed option, and references it to a specific product tag. It is NOT intended as a bill of material for the job.

Product Family - PREC

| Item | Tag(s) | Qty | Description | Model Number |
| --- | --- | --- | --- | --- |
| A1 | RTU-1, RTU-2 | 2 | 6- 25 Ton PKGD Precedent Unitary Rooftop | TSJ180A3S00**000000000000000000000000000 |

| Field Installed Option Description | Part/Ordering Number |
| --- | --- |
| Motorized outside damper 0-50% | FIADMPR102A |
| Horizontal Conversion Panel | FIAHZDC001A |

Product Family - Split System Air Conditioning Units (Small)

| Item | Tag(s) | Qty | Description | Model Number |
| --- | --- | --- | --- | --- |
| B1 | AHU CU-1 | 1 | 1.5 - 5 Ton Unitary Split Systems (SSC) | 4TTR4060N10000*00000*TEM4B0C60S51S*********000**0000*0***000000000000000000000*0**0 |

| Field Installed Option Description | Part/Ordering Number |
| --- | --- |
| 7.21/9.60 kW Htr w/Ckt Brk 208/240/1 | BAYHTR1510BRKC |