554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net

September 25, 2014

Ms. Wendy Ferrill, B.E.

c/o Mississippi State Department of Health

570 East Woodrow Wilson

Jackson, MS 39215-1700

Re:	Dreamland Mobile Home Park, Nicholson Water Association, PWS_ID# 0550041, Pearl 	River County, Ref #116069

Dear Ms. Ferrill,

In reply to the items requested in your correspondence of August 1, 2014, the following information is presented for your consideration.

- The Mississippi DEQ Permit is attached to this submittal.  (item #1 on your letter)

- The Nicholson Water and Sewage Board have modified their May 8, 2014 letter of intent to include the number of Mobile Home lots/sites.  (see the attached letter from Nicholson Water & Sewer Association, Inc., P.O. Box 309, 112 Lilac Drive, Nicholson, MS 39463, (601)-798-9696)

- The Pearl River County Authority has emailed to you their approval of the Dreamland Mobile Home Park Modification/Upgrade project.  A copy of the September 15, 2014 email from Debbie Bounds is attached.

- “Water mains shall be separated from sewer mains by 10’ when running parallel (horizontally) and Water Mains shall be installed 18” above the sewer main (vertically) when crossing.”  This statement can be found on plans sheet C3 and in the water specifications document.

- “Water mains shall be disinfected using a 50 mg/l free chlorine residual for a contact time for 24 hours.”  This statement can be found on plans sheet C3 and in the water specifications document.

- “Microbiological Samples, from the water mains shall be collected by the registered engineer, certified operator or a representative of the Mississippi State Department of Health, the samples shall be analyzed by the Mississippi State Department of Health or a Laboratory Certified by the State.”  This statement can be found on plans sheet C3 and in the water specifications document.

- A title page is attached.

- There are 9 existing mobile homes remaining in the Dreamland Mobile Home Park that have been there for many years. This is an old Mobile Home Park presenting much outdated water & sewer technology.  Due to the current failing sewer system, and new drinking water regulation requirements, the balance of the existing 31 lots, at this time, are not occupied as the

Pearl River County Health Department will no longer sanction occupancy of the vacant lots/sites until the water and sewer deficiencies for the entire Park have been adequately addressed.  Thus, the need for the rehabilitation/upgrade project and the interconnection with available community water & sewerage from Nicholson.  The project intends to provide 40 metered water connections for the Mobile Home Park. (see plans sheet C3)

Should you have any questions, or if further information if required, please feel free to contact me.

Respectfully,

Brian A. Mistich, P.E.

Mississippi Registration #20971

Dammon Engineering, Inc.

554 Old Spanish Trail

Slidell, LA 70458

985-285-4564

985-641-5950 (fax)

985-285-4564

Bill Kingsmill’s contact information is as follows:

William Kingsmill (kingsmillprop@bellsouth.net)

Cell: (504) 528 3838

1200 Business Highway 190, Suite 13

Covington, LA 70433

Lawrence Wm. Haik, Sr

Republic Commercial Properties, LLC

1539 Royal Palm Dr.

Slidell, LA 70458

(985) 960-7033