## Sheet1
Springs At Fremeaux Pool Calculations
Volume
|  | CALCULATION TOTALS |  |  | NOTES
Description | CU. FT. |  |  |  | Note # | Description
Tanning Ledge (6" water depth) | 147.5 | total water surface area = | 1366 | sq. ft. | 1 | 7.48 gallons of water per cu. Ft.
Pool Steps | 126 | total water volume = | 32609.06 | gallons | 2
4' deep pool area | 485 | skimmers required = | 3 | each | 3 | 4 skimmers due to tanning shelf
3' deep pool area | 686 | minimum flow rate = | 109 | GPM | 4 | 5 hour turnover rate for system design
3.5' deep pool area | 1110
4.5' deep pool area | 1805 | total water surface for sunshelf = | 295 | sq. ft. | 5 | pool finish will be diamond brite
[5 empty] | 6 | pool deck finish is to be non-slip finish
Total cu. Ft. = | 4359.5 |  |  |  | 7 | pool construction of shell is to be determined by others. RCI is only responsible for the design of the plumbing and mechanical systems to accommodate the pool design.
[5 empty] | 8 | 5 inlets minimum
[5 empty] | 9 | PSI conversion factor to head loss (2.31)
Maximum flow Rate
gallons divided by hour | 6521.812
6922 gallons per hour
gallons per minute | 108.6969
116 gallons per minute
Total Dynamic Head
Feet
suction pipe run of 132 ln. ft. from main drian to pump with a 3 " SCH PVC Pipe is .8275 feet. (actaul loss is smaller than 1 foot) | 1.32
TR140 Pentair sand filter friction loss is 19 feet per foot | 13
Filter Valving | 25.41
return pipe run of 144 ln. ft. from filter to inlets, 1 foot (actual loss is smaller than 1 foot) | 1.44
Total Dynamic Head | 41.17