Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830


         985-649-5832

Slidell, LA 70458



Slidell, LA  70459

FAX 985-641-5950

Ashford Place

Monroe, Louisiana

Date of Inspection:  July 29, 2006

Unit 1 and 12 

GENERAL:

1) Spray a mold remediation solution on all wood that was stored outside prior to building the structure.

2) Install nail guards on all 2x4 plates that have plumbing running through them.

3) Install nail guards on top and bottom as required at all electrical panels.

4) Exterior stairs to have open risers.  Open risers are not allowed and must be corrected.

FIRE RATING:

1) Telephone, security and cable outlets in demising walls are not providing fire protection.  All demising walls must meet ½ hour fire rating.   Penetrations in fire-resistant walls/partitions/ceilings are permitted provided such boxes have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing.  Outlet boxes on opposite sides of the wall shall be separated:

A. By a horizontal distance of not less than 24 inches.

B. By solid fire-blocking.

C. By protecting both outlet boxes by listed putty pads or

D. By other approved listed materials and methods.

2) Fire-caulk all openings where wires (power, telephone smoke alarm, security, etc., pass thru rated walls or ceilings.

3) Wrap all ceiling boxes with fire rated putty pads.

4) Some plumbing penetrations are not providing fire protection where penetrating a demising wall.  These penetrations are for a washing machine connection.  

5) Plastic boxes in fire rated ceilings did not provide fire protection.  Penetrating items that connect not more than two stories are permitted provided that the annular space, opening around the penetrating item, is filled with an approved material to resist the free passage of flame and the products of combustion (fire-rated putty pads).

6) Some plumbing penetrations were not fire-caulked where penetrating the floor.  Fire-caulk all holes penetrating ceilings/floors.  

7) Membrane penetrations in fire-resistant ceilings are allowed in annular spaces created by the penetration of a fire sprinkler provided it is covered by a metal escutcheon plate.

ELECTRICAL:

1) Aluminum wire is used as the main feeder from electrical service.  The electrical drawings call for copper conductors for the project.

Building 12 was complete and ready except for a few places that were missed.  They were pointed out to Job Site Superintendent.

Building 1 was not really complete and ready for inspection, as some of the apartments had not been wired, etc.

Jim,

The foreman, Gary, who met us stated that the Fire Marshal inspector on a previous visit had said that he only had to use putty pads on the electrical outlets in walls, not the cables and outlet boxes mentioned above for the telephone, security, etc.  Gary called someone on the telephone and they said they weren’t going to cover them.  If this is so, we really are wasting our time and your money.

In general, you need to understand that all openings in a fire rated assembly have to be protected.  This goes for electrical, security, phones, etc.  

David Dammon

Dammon Engineering

