Ashford Place

Monroe, Louisiana

Date of Inspection:  April 14, 2006

Unit B/ 12 Apartments and Clubhouse

1)  Some of the trusses installed had a yellow noted stating that a bearing wall must be installed under a specific location; however there were no load bearing walls under some of the yellow tags.

2)  Spray a mold remediation solution on all wood that was stored outside prior to building the structure.

3)  Caulk all holes penetrating wood (top plates – firewalls)  

4)  Fire-caulk all sheetrock at roof decks for firewalls and smoke walls.

5)  Seal sheetrock in firewalls and smoke walls where penetrations occur.

6)  Complete all electrical work and coat the main lug connections.

7)  Install smoke alarms.

8)  Close holes under tubs.

9)  Secure all strapping for plumbing lines especially for tubs.

10)  Complete fire-resistance rated sheetrock under stairs in clubhouse.

11)   Install nail guards on all 2x4 plates that have plumbing running through them.

12)   Install nail guards where main power penetrates wooden plates at all electrical panels.

13)   All non-outlets and light fixtures in rated ceilings and rated walls must be installed according to the IBC 2003 requirements:

a. 712.3.2 Membrane penetrations in fire-resistance are permitted in walls/partitions with steel electrical boxes that do not exceed 16 sq. inches in an area provided the total area of such openings does not exceed 100 sq. inches of wall area.  Outlet boxes on opposite sides of the wall shall be separated:

1. By a horizontal distance of not less than 24 inches.

2. By a horizontal distance of not less than the depth of the wall cavity where the wall cavity is filled with cellulose loose fill, rockwool, or slag mineral wool insulation.

3. By solid fire-blocking.

4. By protecting both outlet boxes by listed putty pads.

b. 712.4.3 Nonfire-resistance-rated assembly penetrations of horizontal assemblies without a required fire-resistance rating are permitted provided:

1. Noncombustible penetrating items that connect not more than three stories are permitted provided that the annular space is filled with an approved noncombustible material to resist the free passage of flame and the products of combustion.

2. Penetrating items that connect not more than two stories are permitted provided that the annular space is filled with an approved material to resist the free passage of flame and the products of combustion.

c. 712.4.2 (1) Membrane penetrations that are part of a fire-resistance-rated horizontal assembly are permitted for recessed fixtures as long as such fixture is installed such that the required fire resistance will not be reduced.  Penetrations are allowed by steel, ferrous or copper conduits, electrical outlet boxes, pipes, tubes, vents, concrete, or masonry-penetrating items where the annular space is protected to prevent the free passage of flame and the products of combustion.  Such penetrations shall not exceed an aggregate area of 100 sq. inches in any 100 sq. feet of ceiling area in assemblies tested without penetrations.

d. 712.4.2 (3)  Membrane penetrations in fire-resistance are allowed in annular spaces created by the penetration of a fire sprinkler provided it is covered by a metal escutcheon plate.

